Appendix D

IEEE Reliability Test System

RTS Generator Data

ZZTC:TITLE CARD

S.N.                   DESCRIPTION

1 THIS IS IEEE-RTS SYSTEM

ZZMC:MISCELLANEOUS. LOSS SHARING=0 NO LOSS SHARING=1

SEED  LS  END WKS WHERE WHEN KVS KVT KVL CVT FIN JSTEP JFREQ MAXE IOI IOJ IR IN

W1 IW2 IW3

1345237 1 10 17  39   2   2   1   1   1 .05 10000  24   24   1000  1   1   0 10

ZZLD:SYSTEM DATA. AREA NAME IN FOUR LETTERS.                             LOAD

S.N. AREA NAME  PEAK  LFU  OUTAGE WINDOW  FORBIDDEN PERIOD  SUM OF FLOWS FLOW

(MW)    %  BEG WK  END WK  BEG WK  END WK    CONSTRAINT  AREA

1    'A1  '    1470  0.0    1      52       31      32         9999      1

2    'A2  '    1251  0.0    1      52       31      32         9999      1

3    'A3  '     684  0.0    1      52       31      32         9999      1

ZZUD:UNIT DATA

UN NAME  -UNIT NAME IN SIX LETTERS.FIRST FOUR LETTERS ARE THE PLANT NUMBER AND

AND NEXT TWO NUMBERS IDENTIFY THE  UNIT.

LOC - AREA OF LOCATION,FOUR LETTERS.

CAPI - UNIT CAPACITY DURING ITH SEASON.

DFOR - DERATED FORCED OUTAGE RATE (PER UNIT)

FOR - FORCED OUTAGE RATE.  (PER UNIT)

DER - PERCENT DERATING.  (PERCENT)

P/A -PREDETERMINED(1) OR AUTOMATIC(0) SCHEDULING.

B1,D1 - BEGINNING WEEK AND DURATION OF FIRST OUTAGE.

B2,D2  -BEGINNING WEEK AND DURATION OF SECOND OUTAGE.

S.N. UN NAME  LOC  CAP1 CAP2 CAP3 CAP4 DFOR  FOR   DER P/A B1 D1 B2 D2 BUS# OTG

1 'HYDRO ' 'A1 '  300  300  300  300  0.  0.010   0   1  16  0  0  0  22   1

2 'COAL 1' 'A3 '  192  192  192  192  0.  0.020   0   1   0  0  0  0   1   1

3 'COAL 2' 'A3 '  192  192  192  192  0.  0.020   0   1  30  0  0  0   2   1

4 'FS#6 1' 'A3 '  300  300  300  300  0.  0.040   0   1  20  0  0  0   7   1

5 'COAL 3' 'A1 '  215  215  215  215  0.  0.040   0   1   6  0  0  0  15   1

6 'COAL 4' 'A1 '  155  155  155  155  0.  0.040   0   1  11  0  0  0  16   1

7 'COAL 5' 'A2 '  310  310  310  310  0.  0.040   0   1  26  0  0  0  23   1

8 'FS#6 2' 'A2 '  591  591  591  591  0.  0.050   0   1   8  0  0  0  13   1

9 'FS#6 3' 'A2 '  350  350  350  350  0.  0.080   0   1  31  0  0  0  23   1

10 'NUCL 1' 'A1 '  400  400  400  400  0.  0.120   0   1  10  0  0  0  18   1

11 'NUCL 2' 'A1 '  400  400  400  400  0.  0.120   0   1  35  0  0  0  21   1

ZZFC:FIRM CONTRACTS. AREA INDICATED BY FOUR LETTERS.

S.N.  FROM  AREA   TO  AREA    BEG  DAY   END  DAY      MW

ZZOD:UNIT OWNERSHIP DATA

S.N.     UN NAME                     PERCENT OWNERSHIP OF AREA

1     2     3     4

ZZTD:LINE DATA

S.N.     LINE NUMBER   FROM  TO  ADM  CAP  CAPR  PROB (STATE 1)

ADM  CAP  CAPR  PROB (STATE 2)

ADM  CAP  CAPR  PROB (STATE 3)

ADM  CAP  CAPR  PROB (STATE 4)

ADM  CAP  CAPR  PROB (STATE 5)

ADM  CAP  CAPR  PROB (STATE 6)

ZZDD:LINE DERATING DATA

S.N.   LINE NUMBER    UNITS DERATING THIS LINE      DERATING FACTORS

UNIT1 UNIT2 UNIT3 UNIT4        FORWARD  BACKWARD

ZZND:TERMINATING CARD

DESCRIPTION OF VARIABLES IN CARD ZZMC

-------------------------------------

VARIABLES FOR CONVERGENCE TEST:

WHERE : 1 = AREA (TO BE SPECIFIED)

2 = POOL

WHEN : 1 = HOURLY STATISTICS

2 = PEAK STATISTICS

KVS : 1 = LOLE

2 = EUE (USED ONLY WITH HOURLY STATS)

KVT : 1 = WEIGHTED AVERAGE OF STATS, CONSIDERING FORECAST ERROR)

2 = USE ONLY THE NO FORECAST ERROR STATISTIC

KVL : AREA NUMBER (USED ONLY IF KWHERE = 1)

CVT : 0 = STOP WHEN STANDARD DEVIATION OF THE TESTED STATISTIC

IS LESS THAN (.025*MEAN),I.E.,WHEN WE ARE 95% CONFIDENT

THE ESTIMATE IS WITHIN 5% OF TRUE VALUE.

>0 = STOP WHEN STANDARD DEVIATION IS LESS THAN CVTEST.

FIN : TIME TO END SIMULATION IF NO CONVERGENCE. IT SHOULD BE

MULTIPLE OF 8760.

OTHER VARIABLES:

JSTEP : 1 = COLLECT STATS EVERY HOUR.

24 = DAILY PEAK STATS ONLY.

JFREQ : 1 = USE HOURLY MONTE CARLO DRAWS OF GENERATOR AND LINE STATUS.

24 = USE DAILY MONTE CARLO DRAWS.

MAXE  : DEFINES THE UPPER LIMIT OF THE PROB DISTRIBUTION OF EUE.

IOI    : 0 = DO NOT PRINT TRANSMISSION MOD RESULTS.

1 = PRINT TRANSMISSION MOD RESULTS.

IOJ    : 0 = DO NOT PRINT AFTER EACH REPLICATION

IR     : 0 = NEW RUN

1 = RESTART

IN     :     INTERNAL, IN NUMBER OF REPLICATIONS, FOR STORING

THE CONTENTS OF ARRAYS FOR RESTART.

1 = PRINT AFTER EACH REPLICATION

RTS Line Data

IEEE RELIABILITY TEST SYSTEM   100.0 0    0  1979 IEEE RTS

*bus     bus          0    volts  angle    load     load       generation      class desired  gener.-MVAR   shunt P.U. mhos reg. item

*no.     name    area  type P.U.   deg.     MW      MVAR       MW     MVAR      kV     kV     max.    min.    real reactive bus#  no.

*--- ------------ -- -- -- ------ ------ -------- -------- -------- --------  ------ ------ ------- ------- ------- ------- ---- ----

BUS DATA FOLLOWS                     24 ITEMS

1 CT & COAL1 8  3  0  2 1.0200   0.00   108.00    22.00   180.00   10.00   138.00 1.0200   70.00  -50.00  0.0000  0.0000    1    1

2 CT & COAL2 8  3  0  2 1.0200   0.00    97.00    20.00   180.00   10.00   138.00 1.0200   70.00  -50.00  0.0000  0.0000    2    2

3 A1 TIE 3   8  2  0  0 1.0000   0.00   180.00    37.00     0.00    0.00   138.00 0.0000    0.00    0.00  0.0000  0.0000    0    3

4 LOAD BUS 4 8  2  0  0 1.0000   0.00    74.00    15.00     0.00    0.00   138.00 0.0000    0.00    0.00  0.0000  0.0000    0    4

5 LOAD BUS 5 8  3  0  0 1.0000   0.00    71.00    14.00     0.00    0.00   138.00 0.0000    0.00    0.00  0.0000  0.0000    0    5

6 REACTOR    8  2  0  0 1.0000   0.00   136.00    28.00     0.00    0.00   138.00 0.0000    0.00    0.00  0.0000 -1.0000    0    6

7 RADIAL COAL8  3  0  2 1.0200   0.00   125.00    25.00   250.00   90.00   138.00 1.0200  180.00    0.00  0.0000  0.0000    7    7

8 LOAD BUS 8 8  3  0  0 1.0000   0.00   171.00    35.00     0.00    0.00   138.00 0.0000    0.00    0.00  0.0000  0.0000    0    8

9 A1 TIE 9   8  2  0  0 1.0100   0.00   175.00    36.00     0.00    0.00   138.00 1.0100    0.00    0.00  0.0000  0.0000    0    9

10 A1 TIE 10  8  2  0  0 1.0100   0.00   195.00    40.00     0.00    0.00   138.00 1.0100    0.00    0.00  0.0000  0.0000    0   10

11 A2 TIE 11  0  2  0  0 1.0000   0.00     0.00     0.00     0.00    0.00   230.00 0.0000    0.00    0.00  0.0000  0.0000    0   11

12 A2 TIE 12  0  2  0  0 1.0000   0.00     0.00     0.00     0.00    0.00   230.00 0.0000    0.00    0.00  0.0000  0.0000    0   12

13 STEAM GENS 0  2  0  2 1.0200   0.00   265.00    15.00   470.00  100.00   230.00 1.0200  240.00    0.00  0.0000  0.0000   13   13

14 SYNC COND  0  1  0  2 1.0200   0.00   194.00    39.00     0.00    0.00   230.00 1.0200  200.00  -50.00  0.0000  0.0000   14   14

15 CT & COALS 0  1  0  2 1.0200   0.00   317.00    64.00   150.00    0.00   230.00 1.0200   98.00  -50.00  0.0000  0.0000   15   15

16 COAL ONE   0  1  0  2 1.0200   0.00   100.00    20.00   150.00    0.00   230.00 1.0200   80.00  -50.00  0.0000  0.0000   16   16

17 LOAD BUS17 0  1  0  3 1.0200   0.00     0.00     0.00     0.00    0.00   230.00 0.0000    0.00    0.00  0.0000  0.0000    0   17

18 NUCLEAR 18 0  1  0  2 1.0300   0.00   333.00    68.00   400.00    0.00   230.00 1.0300  200.00  -50.00  0.0000  0.0000   18   18

19 LOAD BUS19 0  1  0  0 1.0000   0.00   181.00    37.00     0.00    0.00   230.00 0.0000    0.00    0.00  0.0000  0.0000    0   19

20 LOAD BUS20 0  1  0  0 1.0000   0.00   128.00    26.00     0.00    0.00   230.00 0.0000    0.00    0.00  0.0000  0.0000    0   20

21 NUCLEAR 21 0  1  0  2 1.0300   0.00     0.00     0.00   400.00    0.00   230.00 1.0300  200.00  -50.00  0.0000  0.0000   21   21

22 HYDRO GENS 0  1  0  2 1.0200   0.00     0.00     0.00   100.00    0.00   230.00 1.0200   36.00  -30.00  0.0000  0.0000   22   22

23 COAL GENS  0  2  0  2 1.0200   0.00     0.00     0.00   600.00    0.00   230.00 1.0200  310.00 -125.00  0.0000  0.0000   23   23

24 A2 TIE 24  0  2  0  0 1.0000   0.00     0.00     0.00     0.00    0.00   230.00 0.0000    0.00    0.00  0.0000  0.0000    0   24

-999

*from to area   I type                              ckt rat % nor   reg.   transformer tap   -------tap-------   ---voltage---  item outg

*bus  bus no. 0 D :     R        jX      P.U. chg  80%   60%   40%  bus  0   ratio   angle   min.   max.  step    min.    max.   no. 0or1

*--- ---- -- -- - -  --------  --------  -------- ----- ----- ----- ---- -  ------  ------ ------ ------ ------  ------ ------  ---- ----

BRANCH DATA FOLLOWS                  38 ITEMS

1    2  0  0 1 0  0.002600  0.013900   0.46110   140   105    70    0 0  0.0000    0.00 0.0000 0.0000 0.0000  0.0000 0.0000     1    0

1    3  0  0 1 0  0.054600  0.211200   0.05720   140   105    70    0 0  0.0000    0.00 0.0000 0.0000 0.0000  0.0000 0.0000     2    0

1    5  0  0 1 0  0.021800  0.084500   0.02290   140   105    70    0 0  0.0000    0.00 0.0000 0.0000 0.0000  0.0000 0.0000     3    0

2    4  0  0 1 0  0.032800  0.126700   0.03430   140   105    70    0 0  0.0000    0.00 0.0000 0.0000 0.0000  0.0000 0.0000     4    0

2    6  0  0 1 0  0.049700  0.192000   0.05200   140   105    70    0 0  0.0000    0.00 0.0000 0.0000 0.0000  0.0000 0.0000     5    0

3    9  0  0 1 0  0.030800  0.119000   0.03220   140   105    70    0 0  0.0000    0.00 0.0000 0.0000 0.0000  0.0000 0.0000     6    0

3   24  0  0 1 2  0.002300  0.083900   0.00000   320   240   160    3 0  1.0000    0.00 1.0000 1.0000 0.0000  0.0000 0.0000     7    0

4    9  0  0 1 0  0.026800  0.103700   0.02810   140   105    70    0 0  0.0000    0.00 0.0000 0.0000 0.0000  0.0000 0.0000     8    0

5   10  0  0 1 0  0.022800  0.088300   0.02390   140   105    70    0 0  0.0000    0.00 0.0000 0.0000 0.0000  0.0000 0.0000     9    0

6   10  0  0 1 0  0.013900  0.060500   2.45900   140   105    70    0 0  0.0000    0.00 0.0000 0.0000 0.0000  0.0000 0.0000    10    0

7    8  0  0 1 0  0.015900  0.061400   0.01660   140   105    70    0 0  0.0000    0.00 0.0000 0.0000 0.0000  0.0000 0.0000    11    0

8    9  0  0 1 0  0.042700  0.165100   0.04470   140   105    70    0 0  0.0000    0.00 0.0000 0.0000 0.0000  0.0000 0.0000    12    0

8   10  0  0 1 0  0.042700  0.165100   0.04470   140   105    70    0 0  0.0000    0.00 0.0000 0.0000 0.0000  0.0000 0.0000    13    0

9   11  0  0 1 2  0.002300  0.083900   0.00000   320   240   160    9 0  1.0000    0.00 0.9000 1.1000 0.0000  0.0000 0.0000    14    0

9   12  0  0 1 2  0.002300  0.083900   0.00000   320   240   160    9 0  1.0000    0.00 0.9000 1.1000 0.0000  0.0000 0.0000    15    0

10   11  0  0 1 2  0.002300  0.083900   0.00000   320   240   160   10 0  1.0000    0.00 0.9000 1.1000 0.0000  0.0000 0.0000    16    0

10   12  0  0 1 2  0.002300  0.083900   0.00000   320   240   160   10 0  1.0000    0.00 0.9000 1.1000 0.0000  0.0000 0.0000    17    0

11   13  0  0 1 0  0.006100  0.047600   0.09990   400   300   200    0 0  0.0000    0.00 0.0000 0.0000 0.0000  0.0000 0.0000    18    0

11   14  0  0 1 0  0.005400  0.041800   0.08790   400   300   200    0 0  0.0000    0.00 0.0000 0.0000 0.0000  0.0000 0.0000    19    0

12   13  0  0 1 0  0.006100  0.047600   0.09990   400   300   200    0 0  0.0000    0.00 0.0000 0.0000 0.0000  0.0000 0.0000    20    0

12   23  0  0 1 0  0.012400  0.096600   0.20300   400   300   200    0 0  0.0000    0.00 0.0000 0.0000 0.0000  0.0000 0.0000    21    0

13   23  0  0 1 0  0.011100  0.086500   0.18180   400   300   200    0 0  0.0000    0.00 0.0000 0.0000 0.0000  0.0000 0.0000    22    0

14   16  0  0 1 0  0.005000  0.038900   0.08180   400   300   200    0 0  0.0000    0.00 0.0000 0.0000 0.0000  0.0000 0.0000    23    0

15   16  0  0 1 0  0.002200  0.017300   0.03640   400   300   200    0 0  0.0000    0.00 0.0000 0.0000 0.0000  0.0000 0.0000    24    0

15   21  0  0 1 0  0.006300  0.049000   0.10300   400   300   200    0 0  0.0000    0.00 0.0000 0.0000 0.0000  0.0000 0.0000    25    0

15   21  0  0 2 0  0.006300  0.049000   0.10300   400   300   200    0 0  0.0000    0.00 0.0000 0.0000 0.0000  0.0000 0.0000    26    0

15   24  0  0 1 0  0.006700  0.051900   0.10910   400   300   200    0 0  0.0000    0.00 0.0000 0.0000 0.0000  0.0000 0.0000    27    0

16   17  0  0 1 0  0.003300  0.025900   0.05450   400   300   200    0 0  0.0000    0.00 0.0000 0.0000 0.0000  0.0000 0.0000    28    0

16   19  0  0 1 0  0.003000  0.023100   0.04850   400   300   200    0 0  0.0000    0.00 0.0000 0.0000 0.0000  0.0000 0.0000    29    0

17   18  0  0 1 0  0.001800  0.014400   0.03030   400   300   200    0 0  0.0000    0.00 0.0000 0.0000 0.0000  0.0000 0.0000    30    0

17   22  0  0 1 0  0.013500  0.105300   0.22120   400   300   200    0 0  0.0000    0.00 0.0000 0.0000 0.0000  0.0000 0.0000    31    0

18   21  0  0 1 0  0.003300  0.025900   0.05450   400   300   200    0 0  0.0000    0.00 0.0000 0.0000 0.0000  0.0000 0.0000    32    0

18   21  0  0 2 0  0.003300  0.025900   0.05450   400   300   200    0 0  0.0000    0.00 0.0000 0.0000 0.0000  0.0000 0.0000    33    0

19   20  0  0 1 0  0.005100  0.039600   0.08330   400   300   200    0 0  0.0000    0.00 0.0000 0.0000 0.0000  0.0000 0.0000    34    0

19   20  0  0 2 0  0.005100  0.039600   0.08330   400   300   200    0 0  0.0000    0.00 0.0000 0.0000 0.0000  0.0000 0.0000    35    0

20   23  0  0 1 0  0.002800  0.021600   0.04550   400   300   200    0 0  0.0000    0.00 0.0000 0.0000 0.0000  0.0000 0.0000    36    0

20   23  0  0 2 0  0.002800  0.021600   0.04550   400   300   200    0 0  0.0000    0.00 0.0000 0.0000 0.0000  0.0000 0.0000    37    0

21   22  0  0 1 0  0.008700  0.067800   0.14240   400   300   200    0 0  0.0000    0.00 0.0000 0.0000 0.0000  0.0000 0.0000    38    0

-999

LOSS ZONES FOLLOWS                    0 ITEMS

-99

*A sbus             MW intg. MW tol.  name

*- ----             -------- ------  ------

INTERCHANGE DATA FOLLOWS              3 ITEMS

1   22                 0.00   1.00  Area 1

2   13                 0.00   1.00  Area 2

3    7                 0.00   1.00  Area 3

-9

TIE LINES FOLLOW                      0 ITEMS

-999

END OF DATA

Convolution Method Simulation Output

File INPUTD:

IEEE RELIABILITY TEST SYSTEM   (GENERATORS COMBINED)

---------------------load flow and zipflow data:

OP3.8X               Output Report File

RTSLINE              IEEE common format load flow data file name

0        0           percent load level in area specified, -1 is all areas

1           flat start load flow option   0=no  1=yes

1           run base case as a maximum load case  0=no  1=yes

12           maximum number of iterations for load flow

4           minimum number of iterations between matrix reformation

.1           bus MW and MVAR solution tolerance for load flow

0           combine parallel lines 1=yes 0=no

1           line ratings: 1=80% 2=60% 3=40%

-1 0 0 0 0 0 0 0 0 0 detailed report in area #  -1=all areas   0=none

-1 0 0 0 0 0 0 0 0 0 zip line outs in area #    -1=all areas   0=none

---------------------probabilistic modeling data:

RTSGEN               file containing generator probability data

o/p 'DISTR.REP' of distribution factors for area name shwn

0           o/p 'SCALE.REP' of dist scaling factors 0=no 1=yes -1=all

0           maximum number of circuits out simultaneously

3           0=none 1=GT 2=Gt 3=gt 4=enumer gt   (-) for line separatin

0.00   0.00      line and auto FOR's respectively

0     0.       virtual generation on every bus in area for factor shown

---------------------change data to be made to the load flow base case

1

Case Title: IEEE RELIABILITY TEST SYSTEM   (GENERATORS COMBINED)

Base MVA              =     100.0

Load Flow Solution Monitor:

Number of buses       =        24      5500 max

Number of generators  =        12

Number of circuits    =        38      6500 max

Number of xformers    =         5      1200 max

Number of areas       =         3        20 max

Swing Bus             =        17

Read load flow data   =   0h  0m  0s

assigning generator: HYDRO          to area:           1 Area 1

assigning generator: COAL 3         to area:           1 Area 1

assigning generator: COAL 4         to area:           1 Area 1

assigning generator: COAL 5         to area:           2 Area 2

assigning generator: FS#6 2         to area:           2 Area 2

assigning generator: FS#6 3         to area:           2 Area 2

assigning generator: NUCL 1         to area:           1 Area 1

assigning generator: NUCL 2         to area:           1 Area 1

No of prob generators =        11       350 max

GENERATION SUMMARY (MW):

A#   AREA   PHYSICAL  EXPORTED  IMPORTED     NET    INTERCHG

--  ------  --------  --------  --------  --------  --------

1  Area 1     1470.        0.        0.     1470.        0.

2  Area 2     1251.        0.        0.     1251.        0.

3  Area 3      684.        0.        0.      684.        0.

Matrix factoring time =   0h  0m  0s

Matrix initial size   =        92     20000 max

Matrix final size     =        76

*************************************

* Generation is at maximum capacity *

* Bus loads have been scaled upward *

* Area interchanges have been reset *

* Generator Qmn/mx is now unlimited *

*************************************

load flow solution monitor ...

iter  0   bus   23  perr=    633.25   bus   23  qerr=    181.79      0.11 sec

iter  1   bus   21  perr=     23.62   bus   23  qerr=    119.40      0.00 sec

iter  2   bus   10  perr=      9.18   bus   13  qerr=     37.31      0.00 sec

iter  3   bus   10  perr=      4.25   bus   13  qerr=     17.05      0.00 sec

iter  4   bus   10  perr=      2.04   bus   13  qerr=      8.00      0.05 sec

iter  5   bus   10  perr=      0.96   bus   13  qerr=      3.72      0.00 sec

iter  6   bus   10  perr=      0.45   bus   13  qerr=      1.73      0.00 sec

iter  7   bus   10  perr=      0.21   bus   13  qerr=      0.80      0.00 sec

iter  8   bus   10  perr=      0.10   bus   13  qerr=      0.37      0.00 sec

iter  9   bus   10  perr=      0.05   bus   13  qerr=      0.17      0.05 sec

iter 10   bus   10  perr=      0.02   bus   13  qerr=      0.08      0.00 sec

a load flow solution has been found

iteration time        =           0 sec

total load flow time  =           1 sec

1

Case Title: IEEE RELIABILITY TEST SYSTEM   (GENERATORS COMBINED)

AREA SUMMARY REPORT:

--FROM--    GENERATION    ---LOAD---     ---LOSS---   INTERCHANGE   ERROR

A#  AREA    MW    MVAR    MW    MVAR     MW    MVAR    MW    MVAR     MW

-- ------ ------ ------ ------ ------  ------ ------ ------ ------  -----

1 Area 1  1470.   415.  1450.   294.   20.20    34.     0.    87.  0.001

2 Area 2  1251.   181.  1223.   318.   27.56   -38.     0.   -99.  0.021

3 Area 3   684.   114.   680.   138.    4.38   -35.     0.    12.  0.000

TOTALS  3405.   711.  3353.   750.   52.15   -39.

1

Case Title: IEEE RELIABILITY TEST SYSTEM   (GENERATORS COMBINED)

LOW VOLTAGE SUMMARY REPORT:

3  A1 TIE 3   8  0.9736              12  A2 TIE 12  0  0.9766

6  REACTOR    8  0.9786               8  LOAD BUS 8 8  0.9811

24  A2 TIE 24  0  0.9868              11  A2 TIE 11  0  0.9882

4  LOAD BUS 4 8  0.9916               5  LOAD BUS 5 8  0.9989

19  LOAD BUS19 0  1.0099               9  A1 TIE 9   8  1.0100

10  A1 TIE 10  8  1.0100              20  LOAD BUS20 0  1.0134

1  CT & COAL1 8  1.0200               2  CT & COAL2 8  1.0200

7  RADIAL COAL8  1.0200              13  STEAM GENS 0  1.0200

14  SYNC COND  0  1.0200              15  CT & COALS 0  1.0200

16  COAL ONE   0  1.0200              22  HYDRO GENS 0  1.0200

23  COAL GENS  0  1.0200              17  LOAD BUS17 0  1.0255

18  NUCLEAR 18 0  1.0300              21  NUCLEAR 21 0  1.0300

1

Case Title: IEEE RELIABILITY TEST SYSTEM   (GENERATORS COMBINED)

HIGH VOLTAGE SUMMARY REPORT:

18  NUCLEAR 18 0  1.0300              21  NUCLEAR 21 0  1.0300

17  LOAD BUS17 0  1.0255               1  CT & COAL1 8  1.0200

2  CT & COAL2 8  1.0200               7  RADIAL COAL8  1.0200

13  STEAM GENS 0  1.0200              14  SYNC COND  0  1.0200

15  CT & COALS 0  1.0200              16  COAL ONE   0  1.0200

22  HYDRO GENS 0  1.0200              23  COAL GENS  0  1.0200

20  LOAD BUS20 0  1.0134               9  A1 TIE 9   8  1.0100

10  A1 TIE 10  8  1.0100              19  LOAD BUS19 0  1.0099

5  LOAD BUS 5 8  0.9989               4  LOAD BUS 4 8  0.9916

11  A2 TIE 11  0  0.9882              24  A2 TIE 24  0  0.9868

8  LOAD BUS 8 8  0.9811               6  REACTOR    8  0.9786

12  A2 TIE 12  0  0.9766               3  A1 TIE 3   8  0.9736

1

Case Title: IEEE RELIABILITY TEST SYSTEM   (GENERATORS COMBINED)

HIGHEST LOADED CIRCUITS SUMMARY REPORT:

6  REACTOR    8  -to-    10  A1 TIE 10  8   Ratg=  140   Pct Load= 131.3

7  RADIAL COAL8  -to-     8  LOAD BUS 8 8   Ratg=  140   Pct Load= 108.5

Case Title: IEEE RELIABILITY TEST SYSTEM   (GENERATORS COMBINED)

X---------------B U S   I N F O R M A T I O N--------------X X----------------L I N E   F L O W S---------------X

--------FROM--------   VOLTAGE     GENERATION    LOAD+SHUNT  ---------TO---------                PCT  RATG

BUS# A#     NAME      MAG  ANGLE   MW    MVAR    MW    MVAR  BUS# A#     NAME       MW    MVAR   CAP   MVA   TAP

---- -- ------------ ----- ----- ------ ------ ------ ------ ---- -- ------------ ------ ------ ----- ----- -----

1  3 CT & COAL1 8 1.020 -21.5  192.0   31.3  128.3   26.1

2  3 CT & COAL2 8    7.9  -25.5   19.   140

3  2 A1 TIE 3   8   -1.7   19.9   14.   140

5  3 LOAD BUS 5 8   57.4   10.7   41.   140

2  3 CT & COAL2 8 1.020 -21.6  192.0   22.4  115.2   23.8

1  3 CT & COAL1 8   -7.9  -22.5   17.   140

4  2 LOAD BUS 4 8   35.9   12.4   27.   140

6  2 REACTOR    8   48.8    8.7   35.   140

3  2 A1 TIE 3   8 0.974 -20.6    0.0    0.0  214.8   44.2

1  3 CT & COAL1 8    2.0  -24.5   18.   140

9  2 A1 TIE 9   8   -4.6  -30.1   22.   140

24  2 A2 TIE 24  0 -212.3   10.5   68.   320 1.000

4  2 LOAD BUS 4 8 0.992 -23.9    0.0    0.0   88.3   17.9

2  3 CT & COAL2 8  -35.4  -14.1   27.   140

9  2 A1 TIE 9   8  -52.9   -3.8   38.   140

5  3 LOAD BUS 5 8 0.999 -24.1    0.0    0.0   84.4   16.6

1  3 CT & COAL1 8  -56.7  -10.3   41.   140

10  2 A1 TIE 10  8  -27.6   -6.4   20.   140

6  2 REACTOR    8 0.979 -26.6    0.0    0.0  162.3  147.7

2  3 CT & COAL2 8  -47.6   -9.2   35.   140

10  2 A1 TIE 10  8 -114.7 -138.5  131.   140

7  3 RADIAL COAL8 1.020 -19.1  300.0   60.6  148.5   29.7

8  3 LOAD BUS 8 8  151.5   30.9  108.   140

8  3 LOAD BUS 8 8 0.981 -24.2    0.0    0.0  203.2   41.6

7  3 RADIAL COAL8 -147.8  -18.4  108.   140

9  2 A1 TIE 9   8  -37.4   -8.6   28.   140

10  2 A1 TIE 10  8  -18.0  -14.5   17.   140

9  2 A1 TIE 9   8 1.010 -20.8    0.0    0.0  208.9   43.0

3  2 A1 TIE 3   8    4.8   28.0   20.   140

4  2 LOAD BUS 4 8   53.7    4.0   38.   140

8  3 LOAD BUS 8 8   38.0    6.7   27.   140

11  2 A2 TIE 11  0 -140.4  -49.8   46.   320 1.084

12  2 A2 TIE 12  0 -165.0  -31.8   52.   320 1.083

10  2 A1 TIE 10  8 1.010 -22.8    0.0    0.0  232.8   47.7

5  3 LOAD BUS 5 8   27.8    4.6   20.   140

6  2 REACTOR    8  116.7  -96.1  107.   140

8  3 LOAD BUS 8 8   18.2   10.9   15.   140

11  2 A2 TIE 11  0 -185.1    6.7   57.   320 1.034

12  2 A2 TIE 12  0 -210.3   26.2   66.   320 1.034

11  2 A2 TIE 11  0 0.988 -13.5    0.0    0.0    0.0    0.0

9  2 A1 TIE 9   8  140.9   71.2   50.   320

10  2 A1 TIE 10  8  185.9   23.5   59.   320

13  2 STEAM GENS 0 -226.8  -29.9   58.   400

14  1 SYNC COND  0 -100.1  -64.7   30.   400

12  2 A2 TIE 12  0 0.977 -12.1    0.0    0.0    0.0    0.0

9  2 A1 TIE 9   8  165.8   59.0   56.   320

10  2 A1 TIE 10  8  211.4   13.3   68.   320

13  2 STEAM GENS 0 -176.9  -64.2   48.   400

23  2 COAL GENS  0 -200.3   -8.1   51.   400

13  2 STEAM GENS 0 1.020  -7.4  591.0  150.4  316.3   17.9

11  2 A2 TIE 11  0  230.1   45.3   57.   400

12  2 A2 TIE 12  0  179.1   71.6   47.   400

23  2 COAL GENS  0 -134.5   15.7   33.   400

14  1 SYNC COND  0 1.020 -11.3    0.0  165.2  224.5   45.1

11  2 A2 TIE 11  0  100.8   61.7   29.   400

16  1 COAL ONE   0 -325.3   58.4   81.   400

15  1 CT & COALS 0 1.020  -3.6  215.0  131.5  366.8   74.1

16  1 COAL ONE   0   50.6   -8.1   13.   400

21  1 NUCLEAR 21 0 -209.4   11.2   51.   400

21  1 NUCLEAR 21 0 -209.4   11.2   51.   400

24  2 A2 TIE 24  0  216.5   43.1   54.   400

16  1 COAL ONE   0 1.020  -4.1  155.0   60.4  115.7   23.1

14  1 SYNC COND  0  330.6  -25.9   81.   400

15  1 CT & COALS 0  -50.5    4.8   12.   400

17  1 LOAD BUS17 0 -282.5   21.7   69.   400

19  1 LOAD BUS19 0   41.7   36.7   14.   400

17  1 LOAD BUS17 0 1.025  -0.1    0.0    0.0    0.0    0.0

16  1 COAL ONE   0  285.0   -7.4   70.   400

18  1 NUCLEAR 18 0 -148.1  -13.9   36.   400

22  1 HYDRO GENS 0 -136.9   21.3   34.   400

18  1 NUCLEAR 18 0 1.030   1.1  400.0  104.8  385.3   78.7

17  1 LOAD BUS17 0  148.5   13.7   36.   400

21  1 NUCLEAR 21 0  -66.9    6.2   16.   400

21  1 NUCLEAR 21 0  -66.9    6.2   16.   400

19  1 LOAD BUS19 0 1.010  -4.6    0.0    0.0  209.4   42.8

16  1 COAL ONE   0  -41.6  -41.0   14.   400

20  1 LOAD BUS20 0  -83.9   -0.9   21.   400

20  1 LOAD BUS20 0  -83.9   -0.9   21.   400

20  1 LOAD BUS20 0 1.013  -2.7    0.0    0.0  148.1   30.1

19  1 LOAD BUS19 0   84.3   -4.9   21.   400

19  1 LOAD BUS19 0   84.3   -4.9   21.   400

23  2 COAL GENS  0 -158.3  -10.2   39.   400

23  2 COAL GENS  0 -158.3  -10.2   39.   400

21  1 NUCLEAR 21 0 1.030   2.0  400.0   12.4    0.0    0.0

15  1 CT & COALS 0  212.1   -1.3   51.   400

15  1 CT & COALS 0  212.1   -1.3   51.   400

18  1 NUCLEAR 18 0   67.0  -10.9   16.   400

18  1 NUCLEAR 18 0   67.0  -10.9   16.   400

22  1 HYDRO GENS 0 -158.3   36.6   39.   400

22  1 HYDRO GENS 0 1.020   8.1  300.0  -59.0    0.0    0.0

17  1 LOAD BUS17 0  139.5  -24.6   35.   400

21  1 NUCLEAR 21 0  160.5  -34.3   40.   400

23  2 COAL GENS  0 1.020  -0.9  660.0   31.0    0.0    0.0

12  2 A2 TIE 12  0  205.5   28.5   51.   400

13  2 STEAM GENS 0  136.5  -19.1   34.   400

20  1 LOAD BUS20 0  159.0   10.8   39.   400

20  1 LOAD BUS20 0  159.0   10.8   39.   400

4  2 A2 TIE 24  0 0.987  -9.9    0.0    0.0    0.0    0.0

3  2 A1 TIE 3   8  213.3   29.5   68.   320

15  1 CT & COALS 0 -213.3  -29.5   55.   400

1

Case Title: IEEE RELIABILITY TEST SYSTEM   (GENERATORS COMBINED)

Probability Flow Solution Monitor:

GENERATOR CROSS REFERENCE

-----PROBABILITY------         ----------LOADFLOW---------

S.N.     NAME     CAP3         BUS#        NAME         MW      AREA

1    HYDRO     300.           22    HYDRO GENS 0    300.     Area 1*

2    COAL 1    192.            1    CT & COAL1 8    192.     Area 3*

3    COAL 2    192.            2    CT & COAL2 8    192.     Area 3*

4    FS#6 1    300.            7    RADIAL COAL8    300.     Area 3*

5    COAL 3    215.           15    CT & COALS 0    215.     Area 1*

6    COAL 4    155.           16    COAL ONE   0    155.     Area 1*

7    COAL 5    310.           23    COAL GENS  0    310.     Area 2*

8    FS#6 2    591.           13    STEAM GENS 0    591.     Area 2*

9    FS#6 3    350.           23    COAL GENS  0    350.     Area 2*

10    NUCL 1    400.           18    NUCLEAR 18 0    400.     Area 1*

11    NUCL 2    400.           21    NUCLEAR 21 0    400.     Area 1*

#full enumeration gens=    11        20 max

total number of gens  =    11       350 max

1

Case Title: IEEE RELIABILITY TEST SYSTEM   (GENERATORS COMBINED)

Probability generation will not be able to serve load

Fast solution using piecewise quadratic math

MW per division       =     6.81000

PQ Convolution Time   =   0h  0m  0s

MW total generation   =     3405.00

MW   Probability.....

3405  7.267130E-01  4.716118E-01  4.534259E-01  4.534259E-01  4.534259E-01

3371  4.534259E-01  4.534259E-01  4.534259E-01  4.534259E-01  4.534259E-01

3337  4.534259E-01  4.534259E-01  4.534259E-01  4.534259E-01  4.534259E-01

3303  4.534259E-01  4.534259E-01  4.534259E-01  4.534259E-01  4.534259E-01

3269  4.534111E-01  4.544645E-01  4.516121E-01  4.392247E-01  4.309142E-01

3235  4.306520E-01  4.306481E-01  4.320103E-01  4.227416E-01  4.100938E-01

3201  4.098670E-01  4.036134E-01  3.919573E-01  3.858721E-01  3.855689E-01

3167  3.855689E-01  3.855689E-01  3.855689E-01  3.855689E-01  3.855689E-01

3133  3.855689E-01  3.855689E-01  3.855684E-01  3.865588E-01  3.751341E-01

3099  3.533769E-01  3.393598E-01  3.345236E-01  3.344941E-01  3.344220E-01

3065  3.377801E-01  3.205884E-01  2.929673E-01  2.865977E-01  2.857254E-01

3030  2.852790E-01  2.848519E-01  2.923455E-01  2.725980E-01  1.911709E-01

2996  1.374785E-01  1.349037E-01  1.348710E-01  1.348706E-01  1.348665E-01

2962  1.349249E-01  1.348223E-01  1.341566E-01  1.333237E-01  1.329090E-01

2928  1.327469E-01  1.327927E-01  1.325139E-01  1.315280E-01  1.302432E-01

2894  1.288511E-01  1.278268E-01  1.270273E-01  1.267733E-01  1.264293E-01

2860  1.254302E-01  1.232754E-01  1.197505E-01  1.172358E-01  1.164685E-01

2826  1.181086E-01  1.139478E-01  9.511317E-02  8.229355E-02  8.116025E-02

2792  7.832849E-02  7.500999E-02  7.392639E-02  7.388473E-02  7.404524E-02

2758  7.350176E-02  7.176344E-02  7.021987E-02  6.947996E-02  6.931724E-02

2724  6.926097E-02  6.965451E-02  6.891192E-02  6.447659E-02  5.902108E-02

2690  5.596461E-02  5.516341E-02  5.500717E-02  5.587304E-02  5.466044E-02

2656  4.769596E-02  4.227765E-02  4.059154E-02  4.044422E-02  4.017462E-02

2622  3.990467E-02  3.974205E-02  3.651654E-02  3.070067E-02  2.755959E-02

2588  2.717111E-02  2.711502E-02  2.710089E-02  2.708646E-02  2.703301E-02

2554  2.689514E-02  2.664457E-02  2.641376E-02  2.622722E-02  2.623157E-02

2520  2.608922E-02  2.511712E-02  2.390800E-02  2.285446E-02  2.229788E-02

2486  2.200196E-02  2.199043E-02  2.186870E-02  2.053075E-02  1.908233E-02

2452  1.852009E-02  1.807542E-02  1.764796E-02  1.776188E-02  1.795418E-02

2418  1.551659E-02  1.123079E-02  9.214912E-03  8.992532E-03  8.636191E-03

2384  8.415597E-03  8.360593E-03  8.397549E-03  8.390578E-03  8.071245E-03

2349  7.550615E-03  7.172403E-03  7.022261E-03  6.992411E-03  6.978894E-03

2315  6.937153E-03  6.713047E-03  6.290857E-03  5.902122E-03  5.720036E-03

2281  5.637267E-03  5.627705E-03  5.607689E-03  5.261954E-03  4.706733E-03

2247  4.269279E-03  4.159817E-03  4.150268E-03  4.056178E-03  3.913688E-03

2213  3.831315E-03  3.738153E-03  3.529588E-03  3.361511E-03  3.310771E-03

2179  3.303141E-03  3.301038E-03  3.238464E-03  3.127001E-03  3.035724E-03

2145  2.986072E-03  2.944991E-03  2.930726E-03  2.936739E-03  2.829074E-03

2111  2.589029E-03  2.301150E-03  2.134844E-03  2.067964E-03  2.067657E-03

2077  2.104138E-03  1.974244E-03  1.618353E-03  1.361241E-03  1.288603E-03

2043  1.252380E-03  1.226484E-03  1.247190E-03  1.207637E-03  9.864523E-04

2009  7.409909E-04  6.544974E-04  6.314339E-04  6.197187E-04  6.153114E-04

1975  6.143379E-04  6.142496E-04  6.000111E-04  5.609796E-04  5.162454E-04

1941  4.884019E-04  4.800001E-04  4.761670E-04  4.664287E-04  4.475614E-04

1907  4.258983E-04  4.072360E-04  3.949273E-04  3.867417E-04  3.790734E-04

1873  3.662165E-04  3.531891E-04  3.389932E-04  3.155909E-04  2.972188E-04

1839  2.911109E-04  2.881908E-04  2.810123E-04  2.721847E-04  2.640473E-04

1805  2.481302E-04  2.294930E-04  2.201725E-04  2.173026E-04  2.192486E-04

1771  2.148458E-04  1.946344E-04  1.693110E-04  1.547627E-04  1.469194E-04

1737  1.442283E-04  1.444045E-04  1.426923E-04  1.330122E-04  1.140450E-04

1703  9.789989E-05  8.971894E-05  8.755108E-05  8.991884E-05  9.027654E-05

1668  7.581046E-05  5.331074E-05  4.017391E-05  3.664831E-05  3.474911E-05

1634  3.386488E-05  3.372307E-05  3.362639E-05  3.269605E-05  3.129931E-05

1600  2.982210E-05  2.883588E-05  2.835125E-05  2.801559E-05  2.742478E-05

1566  2.641518E-05  2.516129E-05  2.356472E-05  2.194635E-05  2.099964E-05

1532  2.051377E-05  2.014474E-05  1.928984E-05  1.792932E-05  1.666896E-05

1498  1.542580E-05  1.464374E-05  1.418011E-05  1.349900E-05  1.273128E-05

1464  1.218827E-05  1.104694E-05  9.467766E-06  8.391040E-06  8.014570E-06

1430  7.944811E-06  7.949066E-06  7.853843E-06  7.413620E-06  6.798280E-06

1396  6.435631E-06  6.268187E-06  6.350557E-06  6.443144E-06  5.807964E-06

1362  4.507221E-06  2.939518E-06  1.992303E-06  1.649232E-06  1.572903E-06

1328  1.544787E-06  1.516237E-06  1.476192E-06  1.417262E-06  1.331791E-06

1294  1.249130E-06  1.204304E-06  1.184852E-06  1.177308E-06  1.143124E-06

1260  1.078644E-06  1.020118E-06  9.587138E-07  9.102191E-07  8.884754E-07

1226  8.875338E-07  8.689819E-07  8.184704E-07  7.390820E-07  6.663714E-07

1192  6.189941E-07  5.963637E-07  5.713254E-07  5.186955E-07  4.638857E-07

1158  4.116589E-07  3.453379E-07  2.832621E-07  2.297894E-07  2.047810E-07

1124  1.985568E-07  1.972473E-07  1.934610E-07  1.865751E-07  1.814998E-07

1090  1.786351E-07  1.774266E-07  1.812558E-07  1.825264E-07  1.579010E-07

1056  1.081840E-07  6.756019E-08  5.172528E-08  4.902879E-08  4.798035E-08

1022  4.631731E-08  4.398329E-08  4.142008E-08  3.875826E-08  3.513252E-08

987  3.171384E-08  2.938033E-08  2.835250E-08  2.764681E-08  2.687845E-08

1

Case Title: IEEE RELIABILITY TEST SYSTEM   (GENERATORS COMBINED)

Probability generation will not be able to serve load

Exact solution using 1 MW grid increment solution

Exact 1 MW convol time=   0h  0m  0s

MW total generation   =     3405.00

MW   Probability.....

3405  7.267130E-01  4.534259E-01  4.534259E-01  4.534259E-01  4.534259E-01

3371  4.534259E-01  4.534259E-01  4.534259E-01  4.534259E-01  4.534259E-01

3337  4.534259E-01  4.534259E-01  4.534259E-01  4.534259E-01  4.534259E-01

3303  4.534259E-01  4.534259E-01  4.534259E-01  4.534259E-01  4.534259E-01

3269  4.534259E-01  4.534259E-01  4.534259E-01  4.306520E-01  4.306520E-01

3235  4.306520E-01  4.306520E-01  4.306520E-01  4.306520E-01  4.083428E-01

3201  4.083428E-01  4.083428E-01  3.855689E-01  3.855689E-01  3.855689E-01

3167  3.855689E-01  3.855689E-01  3.855689E-01  3.855689E-01  3.855689E-01

3133  3.855689E-01  3.855689E-01  3.855689E-01  3.855689E-01  3.855689E-01

3099  3.572740E-01  3.345001E-01  3.345001E-01  3.345001E-01  3.345001E-01

3065  3.345001E-01  3.340353E-01  2.860424E-01  2.860424E-01  2.860424E-01

3030  2.850935E-01  2.850935E-01  2.848658E-01  2.848658E-01  1.358002E-01

2996  1.348706E-01  1.348706E-01  1.348706E-01  1.348706E-01  1.348706E-01

2962  1.348706E-01  1.348706E-01  1.336917E-01  1.336917E-01  1.327427E-01

2928  1.327427E-01  1.327427E-01  1.327427E-01  1.315878E-01  1.306583E-01

2894  1.286779E-01  1.274990E-01  1.274990E-01  1.265501E-01  1.265501E-01

2860  1.246007E-01  1.246007E-01  1.183896E-01  1.173607E-01  1.163705E-01

2826  1.163705E-01  1.163705E-01  8.456132E-02  8.151442E-02  8.127964E-02

2792  8.010069E-02  7.388962E-02  7.388962E-02  7.388962E-02  7.388962E-02

2758  7.388962E-02  7.138108E-02  7.035217E-02  6.936201E-02  6.931288E-02

2724  6.929311E-02  6.926156E-02  6.925681E-02  6.145446E-02  6.140634E-02

2690  5.519527E-02  5.507402E-02  5.507402E-02  5.505423E-02  5.505423E-02

2656  5.360209E-02  4.063467E-02  4.054905E-02  4.049992E-02  4.024113E-02

2622  3.965405E-02  3.900488E-02  3.899549E-02  2.878380E-02  2.722914E-02

2588  2.713704E-02  2.713704E-02  2.708792E-02  2.708792E-02  2.698700E-02

2554  2.698661E-02  2.658425E-02  2.658224E-02  2.622093E-02  2.613680E-02

2520  2.613680E-02  2.448929E-02  2.433180E-02  2.260912E-02  2.232741E-02

2486  2.200420E-02  2.174540E-02  2.174540E-02  2.169519E-02  1.866334E-02

2452  1.864212E-02  1.816537E-02  1.751351E-02  1.751311E-02  1.750011E-02

2418  1.749899E-02  9.238345E-03  9.119665E-03  9.117786E-03  8.794374E-03

2384  8.364616E-03  8.364616E-03  8.360152E-03  8.360152E-03  8.284154E-03

2349  7.613109E-03  7.008326E-03  7.004542E-03  6.991144E-03  6.980362E-03

2315  6.916364E-03  6.812739E-03  6.212045E-03  5.924262E-03  5.683278E-03

2281  5.625240E-03  5.624591E-03  5.516841E-03  5.516021E-03  4.729923E-03

2247  4.163833E-03  4.152794E-03  4.120918E-03  4.116563E-03  3.794220E-03

2213  3.785508E-03  3.776893E-03  3.687701E-03  3.329430E-03  3.304225E-03

2179  3.297386E-03  3.290688E-03  3.288088E-03  3.131137E-03  3.002675E-03

2145  2.980719E-03  2.931131E-03  2.928610E-03  2.905478E-03  2.904970E-03

2111  2.472869E-03  2.470165E-03  2.089069E-03  2.078961E-03  2.056987E-03

2077  2.038300E-03  2.038118E-03  1.683483E-03  1.303497E-03  1.295689E-03

2043  1.257753E-03  1.213223E-03  1.211480E-03  1.209288E-03  1.208768E-03

2009  6.684788E-04  6.468431E-04  6.409687E-04  6.177172E-04  6.147127E-04

1975  6.142309E-04  6.081841E-04  6.060362E-04  5.629905E-04  5.200225E-04

1941  4.821801E-04  4.763508E-04  4.758586E-04  4.583931E-04  4.582573E-04

1907  4.148092E-04  4.138751E-04  3.959437E-04  3.804364E-04  3.788403E-04

1873  3.786497E-04  3.504146E-04  3.490952E-04  3.207289E-04  2.894869E-04

1839  2.883198E-04  2.881893E-04  2.870193E-04  2.651598E-04  2.613152E-04

1805  2.611068E-04  2.190937E-04  2.187095E-04  2.169969E-04  2.158103E-04

1771  2.158089E-04  1.974071E-04  1.774916E-04  1.471556E-04  1.463627E-04

1737  1.440651E-04  1.426158E-04  1.417595E-04  1.410433E-04  1.127334E-04

1703  8.969098E-05  8.885898E-05  8.741945E-05  8.739503E-05  8.711088E-05

1668  8.701689E-05  3.948078E-05  3.784692E-05  3.728554E-05  3.402729E-05

1634  3.374877E-05  3.352226E-05  3.334629E-05  3.334339E-05  3.113308E-05

1600  3.017393E-05  2.878178E-05  2.802214E-05  2.794265E-05  2.787167E-05

1566  2.641110E-05  2.522760E-05  2.402256E-05  2.151071E-05  2.148352E-05

1532  2.023179E-05  2.022223E-05  1.907990E-05  1.861610E-05  1.621368E-05

1498  1.542151E-05  1.484148E-05  1.383337E-05  1.381415E-05  1.190629E-05

1464  1.189243E-05  1.158419E-05  9.965886E-06  8.015180E-06  7.996513E-06

1430  7.965578E-06  7.884774E-06  7.847694E-06  7.582402E-06  6.373858E-06

1396  6.357178E-06  6.277851E-06  6.227196E-06  6.211181E-06  6.198948E-06

1362  3.743861E-06  3.643316E-06  1.701684E-06  1.585940E-06  1.583706E-06

1328  1.533477E-06  1.533149E-06  1.444712E-06  1.426202E-06  1.378705E-06

1294  1.235863E-06  1.189199E-06  1.188401E-06  1.165661E-06  1.153787E-06

1260  1.092424E-06  1.003649E-06  9.427397E-07  9.415247E-07  8.769683E-07

1226  8.769683E-07  8.671662E-07  8.666156E-07  7.191115E-07  6.712120E-07

1192  6.251367E-07  5.753811E-07  5.752888E-07  5.256658E-07  4.760051E-07

1158  3.963978E-07  3.811088E-07  2.806973E-07  1.983624E-07  1.981109E-07

1124  1.966579E-07  1.963564E-07  1.956253E-07  1.880116E-07  1.799043E-07

1090  1.792593E-07  1.766370E-07  1.764499E-07  1.761434E-07  1.550698E-07

1056  1.526136E-07  5.226549E-08  4.933892E-08  4.933892E-08  4.724198E-08

1022  4.724198E-08  4.266584E-08  4.263991E-08  3.896088E-08  3.645319E-08

987  3.226940E-08  2.890458E-08  2.787477E-08  2.706755E-08  2.657362E-08

1

Case Title: IEEE RELIABILITY TEST SYSTEM   (GENERATORS COMBINED)

Probability generation will not be able to serve load

PQ per unit error with respect to 1 MW Booth Baleriaux

3405    0.00000000    0.04010773    0.00000000    0.00000000    0.00000000

3371    0.00000000    0.00000000    0.00000000    0.00000000    0.00000000

3337    0.00000000    0.00000000    0.00000000    0.00000000    0.00000000

3303    0.00000000    0.00000000    0.00000000    0.00000000    0.00000000

3269   -0.00003253    0.00229052   -0.00400028    0.01990646    0.00060892

3235    0.00000000   -0.00000886    0.00315406   -0.01836829    0.00428793

3201    0.00373275   -0.01158206    0.01656891    0.00078647    0.00000000

3167    0.00000000    0.00000000    0.00000000    0.00000000    0.00000000

3133    0.00000000    0.00000000   -0.00000139    0.00256749   -0.02706348

3099   -0.01090804    0.01452820    0.00007012   -0.00001800   -0.00023352

3065    0.00980572   -0.04025618    0.02420955    0.00194134   -0.00110804

3030    0.00065094   -0.00084736    0.02625702   -0.04306529    0.40773690

2996    0.01933596    0.00024572    0.00000298    0.00000000   -0.00003049

2962    0.00040261   -0.00035841    0.00347753   -0.00275193    0.00125255

2928    0.00003109    0.00037662   -0.00172380   -0.00045455   -0.00317700

2894    0.00134527    0.00257085   -0.00369996    0.00176400   -0.00095471

2860    0.00665741   -0.01063621    0.01149473   -0.00106394    0.00084141

2826    0.01493554   -0.02081908    0.12478347    0.00955818   -0.00146886

2792   -0.02212459    0.01516280    0.00049762   -0.00006615    0.00210612

2758   -0.00524921    0.00535665   -0.00188054    0.00170061    0.00006288

2724   -0.00046385    0.00567344   -0.00497994    0.04917687   -0.03884385

2690    0.01393857    0.00162306   -0.00121389    0.01487295   -0.00715268

2656   -0.11018478    0.04043295    0.00104788   -0.00137532   -0.00165273

2622    0.00632023    0.01889938   -0.06357026    0.06659533    0.01213569

2588    0.00125547   -0.00081165    0.00047887   -0.00005384    0.00170466

2554   -0.00338928    0.00226901   -0.00633786    0.00024010    0.00362576

2520   -0.00182040    0.02563710   -0.01741770    0.01085138   -0.00132252

2486   -0.00010175    0.01126800    0.00567006   -0.05367257    0.02245014

2452   -0.00654589   -0.00495167    0.00767658    0.01420432    0.02594680

2418   -0.11328628    0.21567096    0.01044406   -0.01373728   -0.01798687

2384    0.00609490   -0.00048099    0.00447328    0.00363944   -0.02570083

2349   -0.00820875    0.02341175    0.00252969    0.00018117   -0.00021027

2315    0.00300577   -0.01463318    0.01268693   -0.00373715    0.00646773

2281    0.00213814    0.00055370    0.01646734   -0.04605969   -0.00490281

2247    0.02532431    0.00169106    0.00712213   -0.01466893    0.03148702

2213    0.01210071   -0.01025723   -0.04287582    0.00963552    0.00198090

2179    0.00174521    0.00314539   -0.01509195   -0.00132093    0.01100672

2145    0.00179603    0.00472861    0.00072252    0.01075925   -0.02612643

2111    0.04697393   -0.06842220    0.02191165   -0.00528935    0.00518750

2077    0.03230055   -0.03133961   -0.03868789    0.04429946   -0.00546924

2043   -0.00427193    0.01093009    0.02947590   -0.00136508   -0.18391913

2009    0.10847326    0.01183342   -0.01487573    0.00324020    0.00097399

1975    0.00017418    0.00997318   -0.00994168   -0.00357192   -0.00726333

1941    0.01290357    0.00766107    0.00064800    0.01752999   -0.02334042

1907    0.02673305   -0.01604147   -0.00256709    0.01657383    0.00061528

1873   -0.03283559    0.00791784   -0.02893766   -0.01601973    0.02670897

1839    0.00968042    0.00000515   -0.02092891    0.02649322    0.01045516

1805   -0.04969870    0.04746511    0.00668913    0.00140881    0.01593170

1771   -0.00446276   -0.01404541   -0.04609043    0.05169448    0.00380335

1737    0.00113242    0.01254203    0.00657990   -0.05694069    0.01163389

1703    0.09152428    0.00967781    0.00150572    0.02887820    0.03634058

1668   -0.12878454    0.35029629    0.06148415   -0.01709049    0.02121315

1634    0.00344031    0.00599010    0.00839959   -0.01941419    0.00533946

1600   -0.01165997    0.00187955    0.01174463    0.00261053   -0.01603369

1566    0.00015441   -0.00262852   -0.01905859    0.02025227   -0.02252324

1532    0.01393710   -0.00383187    0.01100332   -0.03689189    0.02807967

1498    0.00027778   -0.01332338    0.02506557   -0.02281342    0.06929011

1464    0.02487605   -0.04637805   -0.04998253    0.04689347    0.00225812

1430   -0.00260714    0.00815397    0.00078355   -0.02225973    0.06658794

1396    0.01234085   -0.00153928    0.01981006    0.03734604   -0.06307265

1362    0.20389654   -0.19317527    0.17078325    0.03990810   -0.00682104

1328    0.00737571   -0.01103078    0.02178989   -0.00626783   -0.03402743

1294    0.01073448    0.01270221   -0.00298643    0.00999194   -0.00924147

1260   -0.01261444    0.01640902    0.01694438   -0.03324984    0.01312145

1226    0.01204768    0.00209382   -0.05555547    0.02777110   -0.00721175

1192   -0.00982603    0.03646733   -0.00688952   -0.01325986   -0.02546074

1158    0.03849937   -0.09386002    0.00913736    0.15843216    0.03366877

1124    0.00965598    0.00453719   -0.01106335   -0.00764043    0.00886874

1090   -0.00348209    0.00447001    0.02723654    0.03623714    0.01825740

1056   -0.29112470    0.29263481    0.04836664   -0.00628565    0.01562948

1022   -0.01957302    0.03087840   -0.02860782   -0.00520065   -0.03622944

987   -0.01721629    0.01645918    0.01713824    0.02140064    0.01147108

1

Case Title: IEEE RELIABILITY TEST SYSTEM   (GENERATORS COMBINED)

incremental flow monitor ...

1  HYDRO      300.0  MW   TO STUDY AREA

iter  0   bus   22  perr=    300.00   bus    6  qerr=     13.22

iter  1   bus   15  perr=      4.70   bus    6  qerr=      1.95

iter  2   bus   22  perr=      0.85   bus    6  qerr=      0.23

iter  3   bus    9  perr=      0.03   bus    6  qerr=      0.03

2  COAL 1     192.0  MW   TO STUDY AREA

iter  0   bus    1  perr=    184.65   bus    6  qerr=      8.46

iter  1   bus    1  perr=      7.39   bus    6  qerr=      1.24

iter  2   bus   10  perr=      0.22   bus    6  qerr=      0.16

iter  3   bus   10  perr=      0.02   bus    6  qerr=      0.02

3  COAL 2     192.0  MW   TO STUDY AREA

iter  0   bus    2  perr=    185.40   bus    6  qerr=      8.46

iter  1   bus    2  perr=      9.56   bus    6  qerr=      1.20

iter  2   bus   10  perr=      0.22   bus    6  qerr=      0.16

iter  3   bus   10  perr=      0.02   bus    6  qerr=      0.02

4  FS#6 1     300.0  MW   TO STUDY AREA

iter  0   bus    7  perr=    286.71   bus    6  qerr=     13.22

iter  1   bus    7  perr=     10.48   bus    6  qerr=      1.83

iter  2   bus    7  perr=      0.56   bus    6  qerr=      0.22

iter  3   bus    7  perr=      0.05   bus    6  qerr=      0.03

5  COAL 3     215.0  MW   TO STUDY AREA

iter  0   bus   15  perr=    191.48   bus    6  qerr=      9.47

iter  1   bus   15  perr=      2.95   bus    6  qerr=      1.40

iter  2   bus   15  perr=      0.79   bus    6  qerr=      0.17

iter  3   bus   15  perr=      0.03   bus    6  qerr=      0.02

6  COAL 4     155.0  MW   TO STUDY AREA

iter  0   bus   16  perr=    149.65   bus    6  qerr=      6.83

iter  1   bus   15  perr=      2.28   bus    6  qerr=      1.01

iter  2   bus   16  perr=      0.43   bus    6  qerr=      0.13

iter  3   bus    9  perr=      0.02   bus    6  qerr=      0.02

7  COAL 5     310.0  MW   TO STUDY AREA

iter  0   bus   23  perr=    310.00   bus    6  qerr=     13.66

iter  1   bus    9  perr=      4.04   bus    6  qerr=      1.95

iter  2   bus   23  perr=      1.07   bus    6  qerr=      0.23

iter  3   bus    9  perr=      0.04   bus    6  qerr=      0.03

8  FS#6 2     591.0  MW   TO STUDY AREA

iter  0   bus   13  perr=    535.24   bus    6  qerr=     26.04

iter  1   bus   23  perr=      5.74   bus    6  qerr=      3.48

iter  2   bus   13  perr=      1.60   bus    6  qerr=      0.35

iter  3   bus    9  perr=      0.04   bus    6  qerr=      0.04

9  FS#6 3     350.0  MW   TO STUDY AREA

iter  0   bus   23  perr=    350.00   bus    6  qerr=     15.42

iter  1   bus    9  perr=      4.41   bus    6  qerr=      2.19

iter  2   bus   23  perr=      1.16   bus    6  qerr=      0.25

iter  3   bus    9  perr=      0.04   bus    6  qerr=      0.03

10  NUCL 1     400.0  MW   TO STUDY AREA

iter  0   bus   18  perr=    354.03   bus    6  qerr=     17.62

iter  1   bus   15  perr=      6.66   bus    6  qerr=      2.59

iter  2   bus   18  perr=      0.70   bus    6  qerr=      0.28

iter  3   bus    9  perr=      0.04   bus    6  qerr=      0.03

11  NUCL 2     400.0  MW   TO STUDY AREA

iter  0   bus   21  perr=    400.00   bus    6  qerr=     17.62

iter  1   bus   15  perr=      7.95   bus    6  qerr=      2.58

iter  2   bus   21  perr=      1.19   bus    6  qerr=      0.28

iter  3   bus    9  perr=      0.04   bus    6  qerr=      0.03

1  Area 1    1449.8  MW   TO STUDY AREA

iter  0   bus   18  perr=    109.35   bus    6  qerr=     31.94

iter  1   bus   14  perr=      9.63   bus    6  qerr=      4.45

iter  2   bus   13  perr=      0.60   bus    6  qerr=      0.40

iter  3   bus   10  perr=      0.03   bus    6  qerr=      0.04

2  Area 2    1223.4  MW   TO STUDY AREA

iter  0   bus   13  perr=    100.44   bus    6  qerr=     46.91

iter  1   bus    3  perr=      8.17   bus    6  qerr=      6.41

iter  2   bus   18  perr=      0.79   bus    6  qerr=      1.20

iter  3   bus    6  perr=      0.15   bus    6  qerr=      0.23

iter  4   bus    6  perr=      0.03   bus    6  qerr=      0.05

3  Area 3     679.6  MW   TO STUDY AREA

iter  0   bus    8  perr=     80.99   bus    8  qerr=     16.58

iter  1   bus    9  perr=      4.82   bus    6  qerr=      2.20

iter  2   bus    9  perr=      0.36   bus    6  qerr=      0.26

iter  3   bus   18  perr=      0.02   bus    6  qerr=      0.03

average weighted scale factor =    0.84 %

creating GENY.BIN

Gen-line dist fac time=   0h  0m  0s

1

Case Title: IEEE RELIABILITY TEST SYSTEM   (GENERATORS COMBINED)

MAXIMUM PROBABILISTIC CIRCUIT LOADS WITH ALL LINES IN SERVICE

-------FROM------  -------TO--------  RATG   PCT   -GENERATION- to -LOAD-  DIST

7 RADIAL COAL8     8 LOAD BUS 8 8   140  201.4  RADIAL COAL8 -> Area 3  .771

8 LOAD BUS 8 8     9 A1 TIE 9   8   140 -125.6  CT & COAL2 8 -> Area 3  .258

6 REACTOR    8    10 A1 TIE 10  8   140 -121.5  STEAM GENS 0 -> Area 2  .120

14 SYNC COND  0    16 COAL ONE   0   400 -117.9  COAL GENS  0 -> Area 2  .187

16 COAL ONE   0    17 LOAD BUS17 0   400 -116.2  NUCLEAR 18 0 -> Area 1  .375

8 LOAD BUS 8 8    10 A1 TIE 10  8   140 -111.9  CT & COAL1 8 -> Area 3  .269

16 COAL ONE   0    19 LOAD BUS19 0   400  106.1  COAL ONE   0 -> Area 1  .241

8 LOAD BUS 8 8    10 A1 TIE 10  8   140   98.9  RADIAL COAL8 -> Area 3  .267

8 LOAD BUS 8 8     9 A1 TIE 9   8   140   98.7  RADIAL COAL8 -> Area 3  .244

16 COAL ONE   0    19 LOAD BUS19 0   400  -95.7  COAL GENS  0 -> Area 2  .343

4 LOAD BUS 4 8     9 A1 TIE 9   8   140  -95.0  RADIAL COAL8 -> Area 3  .116

7 RADIAL COAL8     8 LOAD BUS 8 8   140  -94.5  CT & COAL2 8 -> Area 3  .214

3 A1 TIE 3   8    24 A2 TIE 24  0   320  -91.0  COAL GENS  0 -> Area 2  .160

10 A1 TIE 10  8    12 A2 TIE 12  0   320  -90.0  STEAM GENS 0 -> Area 2  .173

5 LOAD BUS 5 8    10 A1 TIE 10  8   140  -88.7  RADIAL COAL8 -> Area 3  .195

10 A1 TIE 10  8    11 A2 TIE 11  0   320  -87.7  STEAM GENS 0 -> Area 2  .164

15 CT & COALS 0    16 COAL ONE   0   400   82.6  CT & COALS 0 -> Area 1  .461

11 A2 TIE 11  0    14 SYNC COND  0   400  -82.2  COAL GENS  0 -> Area 2  .185

1 CT & COAL1 8     2 CT & COAL2 8   140   81.8  CT & COAL1 8 -> Area 3  .424

17 LOAD BUS17 0    18 NUCLEAR 18 0   400  -80.6  NUCLEAR 18 0 -> Area 1  .374

11 A2 TIE 11  0    13 STEAM GENS 0   400  -77.1  STEAM GENS 0 -> Area 2  .321

1 CT & COAL1 8     5 LOAD BUS 5 8   140   76.8  CT & COAL1 8 -> Area 3  .273

1 CT & COAL1 8     2 CT & COAL2 8   140  -76.2  CT & COAL2 8 -> Area 3  .526

13 STEAM GENS 0    23 COAL GENS  0   400  -76.1  COAL GENS  0 -> Area 2  .346

20 LOAD BUS20 0    23 COAL GENS  0   400  -74.2  COAL GENS  0 -> Area 2  .169

20 LOAD BUS20 0    23 COAL GENS  0   400  -74.2  COAL GENS  0 -> Area 2  .169

15 CT & COALS 0    24 A2 TIE 24  0   400   73.7  COAL GENS  0 -> Area 2  .163

12 A2 TIE 12  0    23 COAL GENS  0   400  -72.8  COAL GENS  0 -> Area 2  .304

15 CT & COALS 0    16 COAL ONE   0   400  -69.9  COAL ONE   0 -> Area 1  .316

5 LOAD BUS 5 8    10 A1 TIE 10  8   140   68.9  CT & COAL1 8 -> Area 3  .146

9 A1 TIE 9   8    12 A2 TIE 12  0   320  -67.5  STEAM GENS 0 -> Area 2  .155

15 CT & COALS 0    21 NUCLEAR 21 0   400  -65.0  NUCLEAR 21 0 -> Area 1  .242

15 CT & COALS 0    21 NUCLEAR 21 0   400  -65.0  NUCLEAR 21 0 -> Area 1  .242

9 A1 TIE 9   8    11 A2 TIE 11  0   320  -65.0  STEAM GENS 0 -> Area 2  .145

1 CT & COAL1 8     3 A1 TIE 3   8   140   64.6  CT & COAL1 8 -> Area 3  .117

2 CT & COAL2 8     4 LOAD BUS 4 8   140   63.9  CT & COAL2 8 -> Area 3  .162

19 LOAD BUS19 0    20 LOAD BUS20 0   400  -63.0  COAL GENS  0 -> Area 2  .169

19 LOAD BUS19 0    20 LOAD BUS20 0   400  -63.0  COAL GENS  0 -> Area 2  .169

12 A2 TIE 12  0    13 STEAM GENS 0   400  -61.3  STEAM GENS 0 -> Area 2  .299

4 LOAD BUS 4 8     9 A1 TIE 9   8   140   56.9  CT & COAL2 8 -> Area 3  .164

2 CT & COAL2 8     6 REACTOR    8   140   53.3  CT & COAL2 8 -> Area 3  .145

21 NUCLEAR 21 0    22 HYDRO GENS 0   400  -46.6  HYDRO GENS 0 -> Area 1  .593

16 COAL ONE   0    17 LOAD BUS17 0   400   45.2  COAL ONE   0 -> Area 1  .199

17 LOAD BUS17 0    18 NUCLEAR 18 0   400   43.6  COAL ONE   0 -> Area 1  .191

13 STEAM GENS 0    23 COAL GENS  0   400   42.2  STEAM GENS 0 -> Area 2  .128

6 REACTOR    8    10 A1 TIE 10  8   140   38.9  CT & COAL2 8 -> Area 3  .145

2 CT & COAL2 8     4 LOAD BUS 4 8   140  -38.5  RADIAL COAL8 -> Area 3  .113

18 NUCLEAR 18 0    21 NUCLEAR 21 0   400  -38.3  NUCLEAR 21 0 -> Area 1  .230

18 NUCLEAR 18 0    21 NUCLEAR 21 0   400  -38.3  NUCLEAR 21 0 -> Area 1  .230

17 LOAD BUS17 0    22 HYDRO GENS 0   400  -36.8  HYDRO GENS 0 -> Area 1  .399

18 NUCLEAR 18 0    21 NUCLEAR 21 0   400   21.6  NUCLEAR 18 0 -> Area 1  .184

18 NUCLEAR 18 0    21 NUCLEAR 21 0   400   21.6  NUCLEAR 18 0 -> Area 1  .184

15 CT & COALS 0    21 NUCLEAR 21 0   400   12.3  CT & COALS 0 -> Area 1  .122

15 CT & COALS 0    21 NUCLEAR 21 0   400   12.3  CT & COALS 0 -> Area 1  .122

All lines in svc time =   0h  0m  0s

0 lines outaged

Single line outags tm =   0h  0m  0s

Case Title: IEEE RELIABILITY TEST SYSTEM   (GENERATORS COMBINED)

LINES SELECTED FOR OUTAGE/MONITORING IN PROBABILISTIC MODELS

-------FROM------  -------TO--------  RATG  CNTG%  BASE%  DIST  --OUTAGE--

7 RADIAL COAL8     8 LOAD BUS 8 8   140  201.4  201.4  .771

8 LOAD BUS 8 8     9 A1 TIE 9   8   140 -125.6 -125.6  .258

6 REACTOR    8    10 A1 TIE 10  8   140 -121.5 -121.5  .120

14 SYNC COND  0    16 COAL ONE   0   400 -117.9 -117.9  .187

16 COAL ONE   0    17 LOAD BUS17 0   400 -116.2 -116.2  .375

8 LOAD BUS 8 8    10 A1 TIE 10  8   140 -111.9 -111.9  .269

16 COAL ONE   0    19 LOAD BUS19 0   400  106.2  106.1  .241

4 LOAD BUS 4 8     9 A1 TIE 9   8   140  -95.0  -95.0  .116

3 A1 TIE 3   8    24 A2 TIE 24  0   320  -91.0  -91.0  .160

10 A1 TIE 10  8    12 A2 TIE 12  0   320  -90.0  -90.0  .173

5 LOAD BUS 5 8    10 A1 TIE 10  8   140  -88.8  -88.7  .195

10 A1 TIE 10  8    11 A2 TIE 11  0   320  -87.7  -87.7  .164

15 CT & COALS 0    16 COAL ONE   0   400   82.6   82.6  .461

11 A2 TIE 11  0    14 SYNC COND  0   400  -82.2  -82.2  .185

1 CT & COAL1 8     2 CT & COAL2 8   140   81.8   81.8  .424

17 LOAD BUS17 0    18 NUCLEAR 18 0   400  -80.6  -80.6  .374

11 A2 TIE 11  0    13 STEAM GENS 0   400  -77.1  -77.1  .321

1 CT & COAL1 8     5 LOAD BUS 5 8   140   76.8   76.8  .273

13 STEAM GENS 0    23 COAL GENS  0   400  -76.1  -76.1  .346

20 LOAD BUS20 0    23 COAL GENS  0   400  -74.2  -74.2  .169

20 LOAD BUS20 0    23 COAL GENS  0   400  -74.2  -74.2  .169

15 CT & COALS 0    24 A2 TIE 24  0   400   73.7   73.7  .163

12 A2 TIE 12  0    23 COAL GENS  0   400  -72.8  -72.8  .304

9 A1 TIE 9   8    12 A2 TIE 12  0   320  -67.5  -67.5  .155

15 CT & COALS 0    21 NUCLEAR 21 0   400  -65.0  -65.0  .242

15 CT & COALS 0    21 NUCLEAR 21 0   400  -65.0  -65.0  .242

9 A1 TIE 9   8    11 A2 TIE 11  0   320  -65.0  -65.0  .145

1 CT & COAL1 8     3 A1 TIE 3   8   140   64.6   64.6  .117

2 CT & COAL2 8     4 LOAD BUS 4 8   140   63.9   63.9  .162

19 LOAD BUS19 0    20 LOAD BUS20 0   400  -63.0  -63.0  .169

19 LOAD BUS19 0    20 LOAD BUS20 0   400  -63.0  -63.0  .169

12 A2 TIE 12  0    13 STEAM GENS 0   400  -61.3  -61.3  .299

2 CT & COAL2 8     6 REACTOR    8   140   53.3   53.3  .145

21 NUCLEAR 21 0    22 HYDRO GENS 0   400  -46.6  -46.6  .593

18 NUCLEAR 18 0    21 NUCLEAR 21 0   400  -38.3  -38.3  .230

18 NUCLEAR 18 0    21 NUCLEAR 21 0   400  -38.3  -38.3  .230

17 LOAD BUS17 0    22 HYDRO GENS 0   400  -36.8  -36.8  .399

1

Case Title: IEEE RELIABILITY TEST SYSTEM   (GENERATORS COMBINED)

LINES SELECTED FOR OUTAGE/MONITORING IN PROBABILISTIC MODELS

--#-  -------FROM------  -------TO--------  OUT MON

1     1 CT & COAL1 8     2 CT & COAL2 8   0   1

2     1 CT & COAL1 8     3 A1 TIE 3   8   0   1

3     1 CT & COAL1 8     5 LOAD BUS 5 8   0   1

4     2 CT & COAL2 8     4 LOAD BUS 4 8   0   1

5     2 CT & COAL2 8     6 REACTOR    8   0   1

6     3 A1 TIE 3   8    24 A2 TIE 24  0   0   1

7     4 LOAD BUS 4 8     9 A1 TIE 9   8   0   1

8     5 LOAD BUS 5 8    10 A1 TIE 10  8   0   1

9     6 REACTOR    8    10 A1 TIE 10  8   0   1

10     7 RADIAL COAL8     8 LOAD BUS 8 8   0   1

11     8 LOAD BUS 8 8     9 A1 TIE 9   8   0   1

12     8 LOAD BUS 8 8    10 A1 TIE 10  8   0   1

13     9 A1 TIE 9   8    11 A2 TIE 11  0   0   1

14     9 A1 TIE 9   8    12 A2 TIE 12  0   0   1

15    10 A1 TIE 10  8    11 A2 TIE 11  0   0   1

16    10 A1 TIE 10  8    12 A2 TIE 12  0   0   1

17    11 A2 TIE 11  0    13 STEAM GENS 0   0   1

18    11 A2 TIE 11  0    14 SYNC COND  0   0   1

19    12 A2 TIE 12  0    13 STEAM GENS 0   0   1

20    12 A2 TIE 12  0    23 COAL GENS  0   0   1

21    13 STEAM GENS 0    23 COAL GENS  0   0   1

22    14 SYNC COND  0    16 COAL ONE   0   0   1

23    15 CT & COALS 0    16 COAL ONE   0   0   1

24    15 CT & COALS 0    21 NUCLEAR 21 0   0   1

25    15 CT & COALS 0    21 NUCLEAR 21 0   0   1

26    15 CT & COALS 0    24 A2 TIE 24  0   0   1

27    16 COAL ONE   0    17 LOAD BUS17 0   0   1

28    16 COAL ONE   0    19 LOAD BUS19 0   0   1

29    17 LOAD BUS17 0    18 NUCLEAR 18 0   0   1

30    17 LOAD BUS17 0    22 HYDRO GENS 0   0   1

31    18 NUCLEAR 18 0    21 NUCLEAR 21 0   0   1

32    18 NUCLEAR 18 0    21 NUCLEAR 21 0   0   1

33    19 LOAD BUS19 0    20 LOAD BUS20 0   0   1

34    19 LOAD BUS19 0    20 LOAD BUS20 0   0   1

35    20 LOAD BUS20 0    23 COAL GENS  0   0   1

36    20 LOAD BUS20 0    23 COAL GENS  0   0   1

37    21 NUCLEAR 21 0    22 HYDRO GENS 0   0   1

writing line outage file, size in bytes=     10952.0

1

Case Title: IEEE RELIABILITY TEST SYSTEM   (GENERATORS COMBINED)

BEGIN LARGE SYSTEM ANALYSIS OF ALL GENERATION STATES

number of lines outaged                       =        0      500 max

maximum number of lines out simultaneously    =        0

number of generators outaged                  =       11      350 max

number of load areas                          =        3

total probability of all line states run      = 1.0000E+00

total probability of all line states not run  = 0.0000E+00

probability outaged lines are in service      = 1.0000E+00

probability outaged generators are in service = 5.4657E-01

probability outaged lines & gens are in servc = 5.4657E-01

maximum number of transmission line states    = 1.000e   0

maximum number of generator states            = 2.048e   3

maximum number of generator and line states   = 2.048e   3

***********************************************

analyzing system for number of circuits out = 0

***********************************************

line overloaded :     -121.5%         6-  10     REACTOR    8 - A1 TIE 10  8

9 ratg= -140. MW    max loading=  170. MW    min loading=  -54. MW

genr prob=0.019849767908   line prob=1.000000000000   prob ovld=0.019849767908

GENERATOR        LOAD AREA    DIST FACT    LINE MW     SHED MW

8 FS#6 2        2 Area 2    0.119815      30.147     251.609

line overloaded :      201.4%         7-   8     RADIAL COAL8 - LOAD BUS 8 8

10 ratg=  140. MW    max loading=  282. MW    min loading= -132. MW

genr prob=0.959999978542   line prob=1.000000000000   prob ovld=0.959999978542

GENERATOR        LOAD AREA    DIST FACT    LINE MW     SHED MW

4 FS#6 1        3 Area 3    0.771175     141.921     184.032

line overloaded :     -125.6%         8-   9     LOAD BUS 8 8 - A1 TIE 9   8

11 ratg= -140. MW    max loading=  176. MW    min loading= -138. MW

genr prob=0.037219222635   line prob=1.000000000000   prob ovld=0.037219222635

GENERATOR        LOAD AREA    DIST FACT    LINE MW     SHED MW

3 COAL 2        3 Area 3    0.257523      35.806     139.041

line overloaded :     -111.9%         8-  10     LOAD BUS 8 8 - A1 TIE 10  8

12 ratg= -140. MW    max loading=  157. MW    min loading= -139. MW

genr prob=0.027282841504   line prob=1.000000000000   prob ovld=0.027282841504

GENERATOR        LOAD AREA    DIST FACT    LINE MW     SHED MW

2 COAL 1        3 Area 3    0.269315      16.611      61.678

line overloaded :     -117.9%        14-  16     SYNC COND  0 - COAL ONE   0

22 ratg= -400. MW    max loading=  472. MW    min loading= -144. MW

genr prob=0.002614508849   line prob=1.000000000000   prob ovld=0.002614508849

GENERATOR        LOAD AREA    DIST FACT    LINE MW     SHED MW

7 COAL 5        2 Area 2    0.186704      57.878     310.000

9 FS#6 3        2 Area 2    0.186683      13.705      73.413

line overloaded :     -116.2%        16-  17     COAL ONE   0 - LOAD BUS17 0

27 ratg= -400. MW    max loading=  465. MW    min loading= -181. MW

genr prob=0.000059342696   line prob=1.000000000000   prob ovld=0.000059342696

GENERATOR        LOAD AREA    DIST FACT    LINE MW     SHED MW

10 NUCL 1        1 Area 1    0.374526      64.703     172.761

line overloaded :      106.1%        16-  19     COAL ONE   0 - LOAD BUS19 0

28 ratg=  400. MW    max loading=  425. MW    min loading= -383. MW

genr prob=0.000028012735   line prob=1.000000000000   prob ovld=0.000028012735

HYDRO                  1Area 1

GENERATOR        LOAD AREA    DIST FACT    LINE MW     SHED MW

6 COAL 4        1 Area 1    0.240998      24.595     102.056

*******************DEFINITIONS************************

I3=line number to unload in selected line outage table

IG=generator number in INPUTB file in which to shed MW

J3=firm power contract number in INPUTB file

IA=area number in loadflow data in which to shed MW

T1=per unit power in line I3 from IG to IA shedding

T5=+1 or -1 for forward or reverse line flow in I3

DX=increment of MW unloaded in line I3

T6=the total MW unloaded in I3

T4=MW load shed for this column slice

PROB=ENG/DX, average incremental probability

ENG=energy in MWH associated with PROB column slice

******************************************************

unload line     :           7  RADIAL COAL8  -           8  LOAD BUS 8 8

I3  IG  J3  IA     T1    T5   DX      T6      T4      PROB         ENG

10   4   0   3  0.77118  1.  14.2   154.2    18.4  0.7852E+00  0.1114E+02

10   4   0   3  0.77118  1.  14.2   168.4    18.4  0.3158E+00  0.4482E+01

10   4   0   3  0.77118  1.  14.2   182.6    18.4  0.8102E-01  0.1150E+01

10   4   0   3  0.77118  1.  14.2   196.8    18.4  0.1607E-01  0.2281E+00

10   4   0   3  0.77118  1.  14.2   211.0    18.4  0.2209E-02  0.3135E-01

10   4   0   3  0.77118  1.  14.2   225.2    18.4  0.1797E-03  0.2550E-02

10   4   0   3  0.77118  1.  14.2   239.3    18.4  0.8117E-05  0.1152E-03

10   4   0   3  0.77118  1.  14.2   253.5    18.4  0.1715E-06  0.2434E-05

10   4   0   3  0.77118  1.  14.2   267.7    18.4  0.1093E-08  0.1551E-07

10   4   0   3  0.77118  1.  14.2   281.9    18.4  0.1285E-11  0.1824E-10

line is unloaded:        XMW=     153.431            XMWH=     22.0928

from peak:         MW=     3105.00              % =     91.1894

unload line     :           8  LOAD BUS 8 8  -           9  A1 TIE 9   8

I3  IG  J3  IA     T1    T5   DX      T6      T4      PROB         ENG

11   3   0   3  0.25752 -1.   3.6   143.6    13.9  0.3677E-01  0.1317E+00

11   3   0   3  0.25752 -1.   3.6   147.2    13.9  0.3538E-01  0.1267E+00

11   3   0   3  0.25752 -1.   3.6   150.7    13.9  0.3520E-01  0.1260E+00

11   3   0   3  0.25752 -1.   3.6   154.3    13.9  0.2988E-01  0.1070E+00

11   3   0   3  0.25752 -1.   3.6   157.9    13.9  0.2770E-01  0.9918E-01

11   3   0   3  0.25752 -1.   3.6   161.5    13.9  0.2574E-01  0.9217E-01

11   3   0   3  0.25752 -1.   3.6   165.1    13.9  0.2486E-01  0.8901E-01

11   3   0   3  0.25752 -1.   3.6   168.6    13.9  0.2389E-01  0.8553E-01

11   3   0   3  0.25752 -1.   3.6   172.2    13.9  0.2278E-01  0.8158E-01

11   3   0   3  0.25752 -1.   3.6   175.8    13.9  0.2160E-01  0.7733E-01

line is unloaded:        XMW=     156.021            XMWH=     3.94586

from peak:         MW=     300.000              % =     8.81057

unload line     :           6  REACTOR    8  -          10  A1 TIE 10  8

I3  IG  J3  IA     T1    T5   DX      T6      T4      PROB         ENG

9   8   0   2  0.11982 -1.   3.0   143.3    25.2  0.1204E-01  0.3629E-01

9   8   0   2  0.11982 -1.   3.0   146.3    25.2  0.8428E-02  0.2541E-01

9   8   0   2  0.11982 -1.   3.0   149.4    25.2  0.3415E-03  0.1029E-02

9   8   0   2  0.11982 -1.   3.0   152.4    25.2  0.2999E-03  0.9041E-03

9   8   0   2  0.11982 -1.   3.0   155.4    25.2  0.2493E-03  0.7515E-03

9   8   0   2  0.11982 -1.   3.0   158.4    25.2  0.2471E-03  0.7451E-03

9   8   0   2  0.11982 -1.   3.0   161.4    25.2  0.2430E-03  0.7325E-03

9   8   0   2  0.11982 -1.   3.0   164.4    25.2  0.2301E-03  0.6938E-03

9   8   0   2  0.11982 -1.   3.0   167.5    25.2  0.2277E-03  0.6863E-03

9   8   0   2  0.11982 -1.   2.7   170.1    22.5  0.2147E-03  0.5789E-03

line is unloaded:        XMW=     144.352            XMWH=    0.566066

from peak:         MW=     384.000              % =     11.2775

unload line     :           8  LOAD BUS 8 8  -          10  A1 TIE 10  8

I3  IG  J3  IA     T1    T5   DX      T6      T4      PROB         ENG

12   2   0   3  0.26932 -1.   0.0   156.6     0.0  0.2147E-03  0.0000E+00

line is unloaded:        XMW=    0.000000E+00        XMWH=    0.000000E+00

from peak:         MW=     300.000              % =     8.81057

unload line     :          14  SYNC COND  0  -          16  COAL ONE   0

I3  IG  J3  IA     T1    T5   DX      T6      T4      PROB         ENG

22   7   0   2  0.18670 -1.   7.2   407.3    38.3  0.2552E-02  0.1827E-01

22   7   0   2  0.18670 -1.   7.2   414.5    38.3  0.1868E-02  0.1337E-01

22   7   0   2  0.18670 -1.   7.2   421.7    38.3  0.1266E-02  0.9065E-02

22   7   0   2  0.18670 -1.   7.2   428.8    38.3  0.1260E-02  0.9019E-02

22   7   0   2  0.18670 -1.   7.2   436.0    38.3  0.9883E-03  0.7075E-02

22   7   0   2  0.18670 -1.   7.2   443.1    38.3  0.5858E-04  0.4193E-03

22   7   0   2  0.18670 -1.   7.2   450.3    38.3  0.5033E-04  0.3603E-03

22   7   0   2  0.18670 -1.   7.2   457.5    38.3  0.1822E-04  0.1304E-03

22   7   0   2  0.18670 -1.   0.6   458.1     3.3  0.5019E-06  0.3070E-06

22   9   0   2  0.18668 -1.   7.2   465.2    38.3  0.4984E-06  0.3568E-05

22   9   0   2  0.18668 -1.   6.4   471.6    34.0  0.4660E-06  0.2962E-05

line is unloaded:        XMW=     415.192            XMWH=    0.309117

from peak:         MW=     1275.00              % =     37.4449

unload line     :          16  COAL ONE   0  -          17  LOAD BUS17 0

I3  IG  J3  IA     T1    T5   DX      T6      T4      PROB         ENG

27  10   0   1  0.37453 -1.   6.5   406.5    17.3  0.2936E-04  0.1900E-03

27  10   0   1  0.37453 -1.   6.5   412.9    17.3  0.1645E-04  0.1064E-03

27  10   0   1  0.37453 -1.   6.5   419.4    17.3  0.7968E-05  0.5155E-04

27  10   0   1  0.37453 -1.   6.5   425.9    17.3  0.3381E-05  0.2188E-04

27  10   0   1  0.37453 -1.   6.5   432.4    17.3  0.4706E-06  0.3045E-05

27  10   0   1  0.37453 -1.   6.5   438.8    17.3  0.2792E-06  0.1806E-05

27  10   0   1  0.37453 -1.   6.5   445.3    17.3  0.5598E-07  0.3622E-06

27  10   0   1  0.37453 -1.   6.5   451.8    17.3  0.8043E-08  0.5204E-07

27  10   0   1  0.37453 -1.   6.5   458.2    17.3  0.1155E-08  0.7471E-08

27  10   0   1  0.37453 -1.   6.5   464.7    17.3  0.7045E-10  0.4558E-09

line is unloaded:        XMW=     408.394            XMWH=    1.001606E-03

from peak:         MW=     2090.00              % =     61.3803

unload line     :          16  COAL ONE   0  -          19  LOAD BUS19 0

I3  IG  J3  IA     T1    T5   DX      T6      T4      PROB         ENG

28   6   0   1  0.24100  1.   2.5   408.3    10.2  0.4573E-05  0.1125E-04

28   6   0   1  0.24100  1.   2.5   410.7    10.2  0.4765E-05  0.1172E-04

28   6   0   1  0.24100  1.   2.5   413.2    10.2  0.4865E-05  0.1197E-04

28   6   0   1  0.24100  1.   2.5   415.7    10.2  0.3031E-05  0.7454E-05

28   6   0   1  0.24100  1.   2.5   418.1    10.2  0.1059E-05  0.2605E-05

28   6   0   1  0.24100  1.   2.5   420.6    10.2  0.2329E-06  0.5728E-06

28   6   0   1  0.24100  1.   2.5   423.0    10.2  0.3847E-07  0.9462E-07

28   6   0   1  0.24100  1.   1.6   424.6     6.4  0.6931E-08  0.1075E-07

line is unloaded:        XMW=     410.932            XMWH=    1.895071E-04

from peak:         MW=     1935.00              % =     56.8282

1

Case Title: IEEE RELIABILITY TEST SYSTEM   (GENERATORS COMBINED)

AREA  1  Area 1:

LOAD%  LOAD-MW   LOLP       TLOP       EUE-MWh    TEUE-MWh    TOTL-MWh  T/G EUE

30.0    441  0.0000000  0.0000000    0.000001    0.000000    0.000001 2.25E-03

31.0    456  0.0000001  0.0000000    0.000002    0.000000    0.000002 1.83E-03

32.0    470  0.0000002  0.0000000    0.000004    0.000000    0.000004 1.04E-03

33.0    485  0.0000002  0.0000000    0.000007    0.000000    0.000007 7.95E-04

34.0    500  0.0000004  0.0000000    0.000011    0.000000    0.000011 7.20E-04

35.0    515  0.0000006  0.0000000    0.000019    0.000000    0.000019 2.88E-03

36.0    529  0.0000009  0.0000000    0.000030    0.000000    0.000030 6.36E-03

37.0    544  0.0000011  0.0000000    0.000044    0.000000    0.000044 7.45E-03

38.0    559  0.0000012  0.0000000    0.000061    0.000000    0.000062 7.73E-03

39.0    573  0.0000015  0.0000000    0.000082    0.000001    0.000083 7.79E-03

40.0    588  0.0000043  0.0000000    0.000114    0.000001    0.000115 7.12E-03

41.0    603  0.0000064  0.0000000    0.000203    0.000001    0.000204 4.93E-03

42.0    617  0.0000079  0.0000001    0.000312    0.000002    0.000314 5.90E-03

43.0    632  0.0000121  0.0000002    0.000449    0.000005    0.000454 1.08E-02

44.0    647  0.0000153  0.0000004    0.000651    0.000010    0.000661 1.58E-02

45.0    662  0.0000205  0.0000004    0.000920    0.000017    0.000937 1.81E-02

46.0    676  0.0000263  0.0000006    0.001257    0.000025    0.001282 1.97E-02

47.0    691  0.0000297  0.0000006    0.001670    0.000033    0.001703 1.97E-02

48.0    706  0.0000338  0.0000007    0.002149    0.000043    0.002192 1.98E-02

49.0    720  0.0000743  0.0000007    0.002783    0.000053    0.002835 1.89E-02

50.0    735  0.0000970  0.0000022    0.004087    0.000084    0.004171 2.06E-02

51.0    750  0.0001442  0.0000040    0.006003    0.000144    0.006146 2.39E-02

52.0    764  0.0002141  0.0000068    0.008474    0.000243    0.008717 2.87E-02

53.0    779  0.0002473  0.0000092    0.011754    0.000378    0.012132 3.22E-02

54.0    794  0.0002909  0.0000090    0.015790    0.000510    0.016300 3.23E-02

55.0    809  0.0003658  0.0000024    0.020573    0.000546    0.021119 2.65E-02

56.0    823  0.0004253  0.0000066    0.026337    0.000643    0.026980 2.44E-02

57.0    838  0.0004880  0.0000125    0.033168    0.000826    0.033994 2.49E-02

58.0    853  0.0006143  0.0000131    0.041501    0.001020    0.042521 2.46E-02

59.0    867  0.0007398  0.0000058    0.050853    0.001105    0.051958 2.17E-02

60.0    882  0.0012477  0.0000019    0.067464    0.001133    0.068597 1.68E-02

61.0    897  0.0020975  0.0000000    0.090519    0.001133    0.091652 1.25E-02

62.0    911  0.0025528  0.0000000    0.122430    0.001133    0.123562 9.25E-03

63.0    926  0.0029801  0.0000000    0.164825    0.001133    0.165958 6.87E-03

64.0    941  0.0033027  0.0000000    0.211378    0.001133    0.212511 5.36E-03

65.0    956  0.0038220  0.0000000    0.262726    0.001133    0.263859 4.31E-03

66.0    970  0.0042428  0.0000000    0.322373    0.001133    0.323506 3.51E-03

67.0    985  0.0056334  0.0000000    0.399010    0.001133    0.400143 2.84E-03

68.0   1000  0.0069255  0.0000000    0.489667    0.001133    0.490800 2.31E-03

69.0   1014  0.0075151  0.0000000    0.593606    0.001133    0.594739 1.91E-03

70.0   1029  0.0084061  0.0000000    0.714554    0.001133    0.715687 1.59E-03

71.0   1044  0.0152976  0.0000000    0.859748    0.001133    0.860881 1.32E-03

72.0   1058  0.0184925  0.0000000    1.120062    0.001133    1.121195 1.01E-03

73.0   1073  0.0219945  0.0000000    1.424062    0.001133    1.425195 7.96E-04

74.0   1088  0.0260651  0.0000000    1.770495    0.001133    1.771628 6.40E-04

75.0   1103  0.0268882  0.0000000    2.158606    0.001133    2.159739 5.25E-04

76.0   1117  0.0271659  0.0000000    2.556586    0.001133    2.557719 4.43E-04

77.0   1132  0.0398974  0.0000000    3.046995    0.001133    3.048127 3.72E-04

78.0   1147  0.0476023  0.0000000    3.653120    0.001133    3.654253 3.10E-04

79.0   1161  0.0559507  0.0000000    4.454803    0.001133    4.455935 2.54E-04

80.0   1176  0.0692798  0.0000001    5.407555    0.001133    5.408688 2.10E-04

81.0   1191  0.0733407  0.0000000    6.441308    0.001133    6.442441 1.76E-04

82.0   1205  0.0779084 -0.0000001    7.535335    0.001132    7.536467 1.50E-04

83.0   1220  0.1179339  0.0000000    8.910650    0.001132    8.911782 1.27E-04

84.0   1235  0.1252442  0.0000000   10.668993    0.001132   10.670125 1.06E-04

85.0   1250  0.1287225  0.0000002   12.535696    0.001135   12.536831 9.05E-05

86.0   1264  0.1327416  0.0000000   14.469161    0.001135   14.470296 7.84E-05

87.0   1279  0.1349223  0.0000000   16.435809    0.001135   16.436945 6.90E-05

88.0   1294  0.1351558  0.0000000   18.418924    0.001135   18.420059 6.16E-05

89.0   1308  0.2852517  0.0000000   22.052998    0.001135   22.054132 5.15E-05

90.0   1323  0.3372858 -0.0000001   26.444802    0.001133   26.445934 4.28E-05

91.0   1338  0.3522168 -0.0000002   31.406615    0.001130   31.407745 3.60E-05

92.0   1352  0.3855689  0.0000004   36.994519    0.001136   36.995655 3.07E-05

93.0   1367  0.3855689  0.0000000   42.662346    0.001136   42.663483 2.66E-05

94.0   1382  0.4097373  0.0000000   48.431824    0.001136   48.432961 2.35E-05

95.0   1397  0.4306520  0.0000000   54.647550    0.001136   54.648685 2.08E-05

96.0   1411  0.4534259  0.0000002   61.163240    0.001140   61.164379 1.86E-05

97.0   1426  0.4534259 -0.0000004   67.828371    0.001133   67.829506 1.67E-05

98.0   1441  0.4534259  0.0000004   74.493693    0.001140   74.494835 1.53E-05

99.0   1455  0.4534259  0.0000000   81.159075    0.001140   81.160217 1.40E-05

100.0   1470  0.7267130 -0.0000004   88.159233    0.001133   88.160362 1.29E-05

Minimum MWH that can be shed =    0.000421

1

Case Title: IEEE RELIABILITY TEST SYSTEM   (GENERATORS COMBINED)

AREA  2  Area 2:

LOAD%  LOAD-MW   LOLP       TLOP       EUE-MWh    TEUE-MWh    TOTL-MWh  T/G EUE

30.0    375  0.0000000  0.0000000    0.000001    0.000000    0.000001 0.00E+00

31.0    388  0.0000001  0.0000000    0.000002    0.000000    0.000002 0.00E+00

32.0    400  0.0000002  0.0000001    0.000004    0.000001    0.000005 0.28

33.0    413  0.0000002  0.0000005    0.000006    0.000008    0.000014  1.3

34.0    425  0.0000004  0.0000005    0.000009    0.000014    0.000023  1.5

35.0    438  0.0000006  0.0000005    0.000016    0.000020    0.000036  1.3

36.0    450  0.0000009  0.0000005    0.000026    0.000027    0.000052  1.0

37.0    463  0.0000011  0.0000005    0.000037    0.000033    0.000070 0.88

38.0    475  0.0000012  0.0000005    0.000052    0.000039    0.000091 0.75

39.0    488  0.0000015  0.0000005    0.000070    0.000045    0.000115 0.65

40.0    500  0.0000043  0.0000005    0.000097    0.000052    0.000148 0.53

41.0    513  0.0000064  0.0000005    0.000173    0.000058    0.000230 0.34

42.0    525  0.0000079  0.0000005    0.000265    0.000064    0.000330 0.24

43.0    538  0.0000121  0.0000005    0.000382    0.000070    0.000452 0.18

44.0    550  0.0000153  0.0000049    0.000554    0.000132    0.000686 0.24

45.0    563  0.0000205  0.0000105    0.000783    0.000264    0.001047 0.34

46.0    575  0.0000263  0.0000105    0.001070    0.000396    0.001466 0.37

47.0    588  0.0000297  0.0000252    0.001421    0.000711    0.002133 0.50

48.0    600  0.0000338  0.0000495    0.001829    0.001330    0.003159 0.73

49.0    613  0.0000743  0.0000495    0.002368    0.001949    0.004318 0.82

50.0    626  0.0000970  0.0000495    0.003478    0.002568    0.006046 0.74

51.0    638  0.0001442  0.0000495    0.005108    0.003188    0.008296 0.62

52.0    651  0.0002141  0.0000495    0.007211    0.003807    0.011018 0.53

53.0    663  0.0002473  0.0000495    0.010003    0.004426    0.014429 0.44

54.0    676  0.0002909  0.0000495    0.013437    0.005045    0.018482 0.38

55.0    688  0.0003658  0.0000495    0.017508    0.005665    0.023173 0.32

56.0    701  0.0004253  0.0000497    0.022413    0.006287    0.028699 0.28

57.0    713  0.0004880  0.0000508    0.028226    0.006922    0.035148 0.25

58.0    726  0.0006143  0.0000508    0.035318    0.007556    0.042875 0.21

59.0    738  0.0007398  0.0007705    0.043277    0.017195    0.060472 0.40

60.0    751  0.0012477  0.0012188    0.057413    0.032442    0.089855 0.57

61.0    763  0.0020975  0.0012191    0.077033    0.047693    0.124727 0.62

62.0    776  0.0025528  0.0012457    0.104190    0.063277    0.167467 0.61

63.0    788  0.0029801  0.0012661    0.140270    0.079116    0.219385 0.56

64.0    801  0.0033027  0.0012658    0.179887    0.094951    0.274838 0.53

65.0    813  0.0038220  0.0012659    0.223585    0.110788    0.334373 0.50

66.0    826  0.0042428  0.0012678    0.274346    0.126647    0.400993 0.46

67.0    838  0.0056334  0.0012679    0.339566    0.142508    0.482074 0.42

68.0    851  0.0069255  0.0012673    0.416717    0.158363    0.575079 0.38

69.0    863  0.0075151  0.0013076    0.505171    0.174721    0.679892 0.35

70.0    876  0.0084061  0.0014407    0.608100    0.192743    0.800843 0.32

71.0    888  0.0152976  0.0016373    0.731663    0.213227    0.944890 0.29

72.0    901  0.0184925  0.0021220    0.953196    0.239773    1.192968 0.25

73.0    913  0.0219945  0.0021174    1.211906    0.266260    1.478166 0.22

74.0    926  0.0260651  0.0018483    1.506727    0.289383    1.796110 0.19

75.0    938  0.0268882  0.0014161    1.837017    0.307098    2.144115 0.17

76.0    951  0.0271659  0.0014182    2.175707    0.324839    2.500546 0.15

77.0    963  0.0398974  0.0012617    2.593054    0.340623    2.933677 0.13

78.0    976  0.0476023  0.0002430    3.108879    0.343663    3.452542 0.11

79.0    988  0.0559507  0.0002576    3.791127    0.346885    4.138013 9.15E-02

80.0   1001  0.0692798  0.0002563    4.601938    0.350092    4.952030 7.61E-02

81.0   1013  0.0733407  0.0002810    5.481684    0.353607    5.835290 6.45E-02

82.0   1026  0.0779084  0.0003079    6.412722    0.357459    6.770181 5.57E-02

83.0   1038  0.1179339  0.0003254    7.583143    0.361529    7.944673 4.77E-02

84.0   1051  0.1252442  0.0003408    9.079529    0.365793    9.445321 4.03E-02

85.0   1063  0.1287225  0.0003462   10.668131    0.370124   11.038255 3.47E-02

86.0   1076  0.1327416  0.0003507   12.313549    0.374511   12.688060 3.04E-02

87.0   1088  0.1349223  0.0003528   13.987206    0.378924   14.366131 2.71E-02

88.0   1101  0.1351558  0.0003548   15.674877    0.383363   16.058241 2.45E-02

89.0   1113  0.2852517  0.0001775   18.767547    0.385583   19.153130 2.05E-02

90.0   1126  0.3372858  0.0000938   22.505061    0.386756   22.891817 1.72E-02

91.0   1138  0.3522168  0.0091494   26.727665    0.501216   27.228880 1.88E-02

92.0   1151  0.3855689  0.0100251   31.483084    0.626630   32.109715 1.99E-02

93.0   1163  0.3855689  0.0110494   36.306519    0.764856   37.071377 2.11E-02

94.0   1176  0.4097373  0.0111553   41.216462    0.904409   42.120872 2.19E-02

95.0   1188  0.4306520  0.0011154   46.506170    0.918362   47.424534 1.97E-02

96.0   1201  0.4534259  0.0000004   52.051154    0.918368   52.969521 1.76E-02

97.0   1213  0.4534259  0.0000000   57.723316    0.918368   58.641682 1.59E-02

98.0   1226  0.4534259  0.0000000   63.395640    0.918368   64.314011 1.45E-02

99.0   1238  0.4534259  0.0000000   69.068014    0.918368   69.986382 1.33E-02

100.0   1251  0.7267130  0.0000000   75.025290    0.918368   75.943657 1.22E-02

Minimum MWH that can be shed =    0.125537

1

Case Title: IEEE RELIABILITY TEST SYSTEM   (GENERATORS COMBINED)

AREA  3  Area 3:

LOAD%  LOAD-MW   LOLP       TLOP       EUE-MWh    TEUE-MWh    TOTL-MWh  T/G EUE

30.0    205  0.0000000  0.0000009    0.000000    0.000185    0.000185 4.17E+02

31.0    212  0.0000001  0.0000174    0.000001    0.000304    0.000305 3.64E+02

32.0    219  0.0000002  0.0000196    0.000002    0.000438    0.000440 2.21E+02

33.0    226  0.0000002  0.0000497    0.000003    0.000778    0.000781 2.37E+02

34.0    233  0.0000004  0.0000788    0.000005    0.001317    0.001322 2.57E+02

35.0    239  0.0000006  0.0000980    0.000009    0.001988    0.001996 2.27E+02

36.0    246  0.0000009  0.0001226    0.000014    0.002826    0.002840 2.02E+02

37.0    253  0.0000011  0.0001379    0.000020    0.003769    0.003790 1.84E+02

38.0    260  0.0000012  0.0001564    0.000028    0.004839    0.004868 1.70E+02

39.0    267  0.0000015  0.0001781    0.000038    0.006057    0.006095 1.58E+02

40.0    274  0.0000043  0.0001977    0.000053    0.007410    0.007463 1.40E+02

41.0    280  0.0000064  0.0002250    0.000094    0.008948    0.009043  95.

42.0    287  0.0000079  0.0002739    0.000145    0.010822    0.010967  75.

43.0    294  0.0000121  0.0003194    0.000209    0.013007    0.013215  62.

44.0    301  0.0000153  0.0003729    0.000303    0.015558    0.015860  51.

45.0    308  0.0000205  0.0004101    0.000428    0.018363    0.018791  43.

46.0    315  0.0000263  0.0007467    0.000585    0.023470    0.024055  40.

47.0    321  0.0000297  0.0010914    0.000777    0.030935    0.031712  40.

48.0    328  0.0000338  0.0016167    0.001000    0.041993    0.042993  42.

49.0    335  0.0000743  0.0018790    0.001295    0.054846    0.056141  42.

50.0    342  0.0000970  0.0020097    0.001902    0.068593    0.070494  36.

51.0    349  0.0001442  0.0021512    0.002793    0.083307    0.086100  30.

52.0    356  0.0002141  0.0023284    0.003943    0.099233    0.103176  25.

53.0    363  0.0002473  0.0024543    0.005469    0.116020    0.121489  21.

54.0    369  0.0002909  0.0026297    0.007347    0.134007    0.141354  18.

55.0    376  0.0003658  0.0029929    0.009573    0.154479    0.164052  16.

56.0    383  0.0004253  0.0040869    0.012255    0.182433    0.194688  15.

57.0    390  0.0004880  0.0047569    0.015433    0.214970    0.230403  14.

58.0    397  0.0006143  0.0052090    0.019311    0.250600    0.269911  13.

59.0    404  0.0007398  0.0056175    0.023662    0.289024    0.312686  12.

60.0    410  0.0012477  0.0070173    0.031391    0.337022    0.368413  11.

61.0    417  0.0020975  0.0115151    0.042119    0.415785    0.457904  9.9

62.0    424  0.0025528  0.0128971    0.056967    0.504001    0.560969  8.8

63.0    431  0.0029801  0.0146299    0.076694    0.604070    0.680764  7.9

64.0    438  0.0033027  0.0162054    0.098356    0.714915    0.813270  7.3

65.0    445  0.0038220  0.0174094    0.122248    0.833995    0.956243  6.8

66.0    451  0.0042428  0.0183289    0.150002    0.959365    1.109367  6.4

67.0    458  0.0056334  0.0178825    0.185662    1.081681    1.267343  5.8

68.0    465  0.0069255  0.0183091    0.227845    1.206915    1.434760  5.3

69.0    472  0.0075151  0.0273475    0.276209    1.393972    1.670181  5.0

70.0    479  0.0084061  0.0350106    0.332486    1.633445    1.965931  4.9

71.0    486  0.0152976  0.0477805    0.400046    1.960264    2.360310  4.9

72.0    492  0.0184925  0.0635930    0.521172    2.395240    2.916412  4.6

73.0    499  0.0219945  0.0623546    0.662625    2.821744    3.484368  4.3

74.0    506  0.0260651  0.0628257    0.823822    3.251472    4.075294  3.9

75.0    513  0.0268882  0.0767440    1.004412    3.776402    4.780814  3.8

76.0    520  0.0271659  0.0836690    1.189595    4.348698    5.538293  3.7

77.0    527  0.0398974  0.0800345    1.417785    4.896135    6.313920  3.5

78.0    534  0.0476023  0.0884567    1.699819    5.501175    7.200994  3.2

79.0    540  0.0559507  0.0849378    2.072847    6.082151    8.154998  2.9

80.0    547  0.0692798  0.0831644    2.516168    6.650996    9.167164  2.6

81.0    554  0.0733407  0.0833367    2.997180    7.221020   10.218201  2.4

82.0    561  0.0779084  0.0823706    3.506237    7.784436   11.290673  2.2

83.0    568  0.1179339  0.1244951    4.146179    8.635978   12.782158  2.1

84.0    575  0.1252442  0.1812029    4.964347    9.875408   14.839755  2.0

85.0    581  0.1287225  0.2085459    5.832935   11.301864   17.134800  1.9

86.0    588  0.1327416  0.2362853    6.732588   12.918058   19.650646  1.9

87.0    595  0.1349223  0.2465391    7.647682   14.604389   22.252069  1.9

88.0    602  0.1351558  0.2313051    8.570437   16.186507   24.756945  1.9

89.0    609  0.2852517  0.1224208   10.261394   17.023866   27.285259  1.7

90.0    616  0.3372858  0.0949801   12.304927   17.673531   29.978458  1.4

91.0    622  0.3522168  0.0714240   14.613688   18.162073   32.775761  1.2

92.0    629  0.3855689  0.0424035   17.213774   18.452113   35.665886  1.1

93.0    636  0.3855689  0.0585031   19.851048   18.852272   38.703320 0.95

94.0    643  0.4097373  0.0522497   22.535621   19.209661   41.745281 0.85

95.0    650  0.4306520  0.0251239   25.427836   19.381508   44.809345 0.76

96.0    657  0.4534259  0.0041654   28.459626   19.409999   47.869625 0.68

97.0    663  0.4534259  0.0610956   31.560952   19.827894   51.388847 0.63

98.0    670  0.4534259  0.3904803   34.662367   22.498764   57.161129 0.65

99.0    677  0.4534259  0.4094042   37.763809   25.299093   63.062901 0.67

100.0    684  0.7267130  0.2425369   41.021025   26.958048   67.979073 0.66

Minimum MWH that can be shed =   18.053553

1

Case Title: IEEE RELIABILITY TEST SYSTEM   (GENERATORS COMBINED)

TOTAL SYSTEM:

LOAD%  LOAD-MW   LOLP       TLOP       EUE-MWh    TEUE-MWh    TOTL-MWh  T/G EUE

30.0   1022  0.0000000  0.0000000    0.000002    0.000005    0.000007  2.3

31.0   1056  0.0000001  0.0000002    0.000004    0.000012    0.000016  2.8

32.0   1090  0.0000002  0.0000003    0.000010    0.000022    0.000032  2.3

33.0   1124  0.0000002  0.0000004    0.000016    0.000034    0.000051  2.1

34.0   1158  0.0000004  0.0000003    0.000025    0.000046    0.000072  1.8

35.0   1192  0.0000006  0.0000004    0.000044    0.000060    0.000104  1.4

36.0   1226  0.0000009  0.0000012    0.000070    0.000100    0.000169  1.4

37.0   1260  0.0000011  0.0000028    0.000102    0.000194    0.000296  1.9

38.0   1294  0.0000012  0.0000030    0.000142    0.000296    0.000438  2.1

39.0   1328  0.0000015  0.0000037    0.000190    0.000422    0.000613  2.2

40.0   1362  0.0000043  0.0000050    0.000263    0.000593    0.000857  2.3

41.0   1396  0.0000064  0.0000066    0.000470    0.000817    0.001287  1.7

42.0   1430  0.0000079  0.0000092    0.000723    0.001130    0.001853  1.6

43.0   1464  0.0000121  0.0000102    0.001040    0.001477    0.002517  1.4

44.0   1498  0.0000153  0.0000092    0.001507    0.001790    0.003297  1.2

45.0   1532  0.0000205  0.0000081    0.002131    0.002064    0.004196 0.97

46.0   1566  0.0000263  0.0000397    0.002912    0.003415    0.006327  1.2

47.0   1600  0.0000297  0.0000663    0.003869    0.005673    0.009541  1.5

48.0   1634  0.0000338  0.0000849    0.004979    0.008562    0.013541  1.7

49.0   1668  0.0000743  0.0000891    0.006446    0.011595    0.018041  1.8

50.0   1703  0.0000970  0.0000770    0.009466    0.014216    0.023682  1.5

51.0   1737  0.0001442  0.0000857    0.013904    0.017135    0.031039  1.2

52.0   1771  0.0002141  0.0001037    0.019628    0.020666    0.040294  1.1

53.0   1805  0.0002473  0.0001352    0.027225    0.025271    0.052496 0.93

54.0   1839  0.0002909  0.0001567    0.036574    0.030605    0.067179 0.84

55.0   1873  0.0003658  0.0001529    0.047654    0.035812    0.083466 0.75

56.0   1907  0.0004253  0.0001492    0.061004    0.040894    0.101898 0.67

57.0   1941  0.0004880  0.0005378    0.076827    0.059205    0.136032 0.77

58.0   1975  0.0006143  0.0008951    0.096131    0.089684    0.185814 0.93

59.0   2009  0.0007398  0.0013115    0.117792    0.134340    0.252132  1.1

60.0   2043  0.0012477  0.0012083    0.156268    0.175481    0.331749  1.1

61.0   2077  0.0020975  0.0008526    0.209671    0.204511    0.414182 0.98

62.0   2111  0.0025528  0.0005580    0.283587    0.223512    0.507099 0.79

63.0   2145  0.0029801  0.0006584    0.381789    0.245929    0.627718 0.64

64.0   2179  0.0033027  0.0011752    0.489621    0.285945    0.775567 0.58

65.0   2213  0.0038220  0.0019817    0.608560    0.353424    0.961983 0.58

66.0   2247  0.0042428  0.0020257    0.746720    0.422397    1.169118 0.57

67.0   2281  0.0056334  0.0013302    0.924237    0.467690    1.391927 0.51

68.0   2315  0.0069255  0.0012057    1.134229    0.508745    1.642973 0.45

69.0   2349  0.0075151  0.0061017    1.374986    0.716509    2.091495 0.52

70.0   2384  0.0084061  0.0106184    1.655139    1.078066    2.733205 0.65

71.0   2418  0.0152976  0.0094691    1.991457    1.400488    3.391946 0.70

72.0   2452  0.0184925  0.0061157    2.594429    1.608727    4.203156 0.62

73.0   2486  0.0219945  0.0041733    3.298591    1.750827    5.049418 0.53

74.0   2520  0.0260651  0.0021097    4.101043    1.822663    5.923706 0.44

75.0   2554  0.0268882  0.0064459    5.000034    2.042148    7.042181 0.41

76.0   2588  0.0271659  0.0142735    5.921886    2.528160    8.450047 0.43

77.0   2622  0.0398974  0.0168888    7.057832    3.103226   10.161057 0.44

78.0   2656  0.0476023  0.0144028    8.461816    3.593638   12.055454 0.42

79.0   2690  0.0559507  0.0069630   10.318774    3.830730   14.149505 0.37

80.0   2724  0.0692798  0.0033012   12.525658    3.943135   16.468792 0.31

81.0   2758  0.0733407  0.0113500   14.920168    4.329602   19.249771 0.29

82.0   2792  0.0779084  0.0347245   17.454288    5.511974   22.966263 0.32

83.0   2826  0.1179339  0.0189732   20.639967    6.158007   26.797974 0.30

84.0   2860  0.1252442  0.0059816   24.712862    6.361681   31.074543 0.26

85.0   2894  0.1287225  0.0033473   29.036755    6.475657   35.512413 0.22

86.0   2928  0.1327416  0.0014947   33.515289    6.526550   40.041840 0.19

87.0   2962  0.1349223  0.0344018   38.070686    7.697933   45.768620 0.20

88.0   2996  0.1351558  0.1435889   42.664227   12.587109   55.251335 0.30

89.0   3030  0.2852517  0.0588517   51.081924   14.591011   65.672935 0.29

90.0   3065  0.3372858  0.0570122   61.254772   16.532280   77.787048 0.27

91.0   3099  0.3522168  0.0496349   72.747948   18.222351   90.970299 0.25

92.0   3133  0.3855689  0.0031145   85.691353   18.328400  104.019753 0.21

93.0   3167  0.3855689  0.0115654   98.819885   18.722198  117.542084 0.19

94.0   3201  0.4097373  0.0294788  112.183876   19.725952  131.909821 0.18

95.0   3235  0.4306520  0.0139242  126.581520   20.200073  146.781586 0.16

96.0   3269  0.4534259  0.0037266  141.673981   20.326965  162.000946 0.14

97.0   3303  0.4534259 -0.0000027  157.112595   20.326874  177.439468 0.13

98.0   3337  0.4534259  0.0000040  172.551651   20.327011  192.878662 0.12

99.0   3371  0.4534259  0.0293896  187.990845   21.327728  209.318573 0.11

100.0   3405  0.7267130  0.1931545  204.205490   27.904648  232.110138 0.14

Minimum MWH that can be shed =   18.179510

:         :          :       :            :                       :

:         :          :       :            :                       :

Installed         :          :       :            : Ratio of unserved energies

Generation         :          :       :            : Transmission to Generation

:          :       :            :

:          :       :            :

Probability of not          :       :   Additional unserved MWH due

serving load at             :       :   to transmission constraints

system peak hour            :       :

:       :

:       :

Probability transmission       Unserved MWH during the peak load hour

will be a bottleneck           due only to insufficient generation

large system analysis completed

# xmissn states examined  =           1

Prob of system separation =    0.0000E+00

Prob of untested states   =    0.0000E+00

Prob of all states tested =    1.000000

Large System run time     0h  0m  4s

Total run time            0h  0m  6s

Linear Program Simulation Output

File INPUTD:

IEEE RELIABILITY TEST SYSTEM   (GENERATORS COMBINED)

---------------------load flow and zipflow data:

OP4.8X               Output Report File

RTSLINE              IEEE common format load flow data file name

0        0           percent load level in area specified, -1 is all areas

1           flat start load flow option   0=no  1=yes

1           run base case as a maximum load case  0=no  1=yes

12           maximum number of iterations for load flow

4           minimum number of iterations between matrix reformation

.1           bus MW and MVAR solution tolerance for load flow

0           combine parallel lines 1=yes 0=no

1           line ratings: 1=80% 2=60% 3=40%

-1 0 0 0 0 0 0 0 0 0 detailed report in area #  -1=all areas   0=none

-1 0 0 0 0 0 0 0 0 0 zip line outs in area #    -1=all areas   0=none

---------------------probabilistic modeling data:

RTSGEN               file containing generator probability data

o/p 'DISTR.REP' of distribution factors for area name shwn

0           o/p 'SCALE.REP' of dist scaling factors 0=no 1=yes -1=all

0           maximum number of circuits out simultaneously

4           0=none 1=GT 2=Gt 3=gt 4=enumer gt   (-) for line separatn

0.00   0.00      line and auto FOR's respectively

0     0.       virtual generation on every bus in area for factor shown

---------------------change data to be made to the load flow base case

Ù

½

****************************************************************************

all load flow output omitted is identical to the previous convolution output

****************************************************************************

½

Ú

1

Case Title: IEEE RELIABILITY TEST SYSTEM   (GENERATORS COMBINED)

BEGIN FULL ENUMERATION OF ALL GENERATION AND LINE STATES

number of lines outaged                       =        0       15 max

maximum number of lines out simultaneously    =        0

number of generators outaged                  =       11       20 max

number of load areas                          =        3

total probability of all line states run      = 1.0000E+00

total probability of all line states not run  = 0.0000E+00

probability outaged lines are in service      = 1.0000E+00

probability outaged generators are in service = 5.4657E-01

probability outaged lines & gens are in servc = 5.4657E-01

maximum number of transmission line states    = 1.000e   0

maximum number of generator states            = 2.048e   3

maximum number of generator and line states   = 2.048e   3

***********************************************

analyzing system for number of circuits out = 0

***********************************************

line state:    1  outage line(s):

generator states: 0000000000 0

line overloaded :      106.9%         7-   8     RADIAL COAL8 - LOAD BUS 8 8

Linear Program Rows   =        27       360 max

Linear Program Columns=        15        50 max

Initial LP:       HYDRO     COAL 1    COAL 2    FS#6 1    COAL 3    COAL 4    COAL 5    FS#6 2    FS#6 3    NUCL 1    NUCL 2    Area 1    Area 2    Area 3

Area:          1         3         3         3         1         1         2         2         2         1         1         1         2         3

MAX              1.0000    1.0000    1.0000    1.0000    1.0000    1.0000    1.0000    1.0000    1.0000    1.0000    1.0000    0.0000    0.0000    0.0000

1  300.0000   -1.0000    0.0000    0.0000    0.0000    0.0000    0.0000    0.0000    0.0000    0.0000    0.0000    0.0000    0.0000    0.0000    0.0000

2  192.0000    0.0000   -1.0000    0.0000    0.0000    0.0000    0.0000    0.0000    0.0000    0.0000    0.0000    0.0000    0.0000    0.0000    0.0000

3  192.0000    0.0000    0.0000   -1.0000    0.0000    0.0000    0.0000    0.0000    0.0000    0.0000    0.0000    0.0000    0.0000    0.0000    0.0000

4  300.0000    0.0000    0.0000    0.0000   -1.0000    0.0000    0.0000    0.0000    0.0000    0.0000    0.0000    0.0000    0.0000    0.0000    0.0000

5  215.0000    0.0000    0.0000    0.0000    0.0000   -1.0000    0.0000    0.0000    0.0000    0.0000    0.0000    0.0000    0.0000    0.0000    0.0000

6  155.0000    0.0000    0.0000    0.0000    0.0000    0.0000   -1.0000    0.0000    0.0000    0.0000    0.0000    0.0000    0.0000    0.0000    0.0000

7  310.0000    0.0000    0.0000    0.0000    0.0000    0.0000    0.0000   -1.0000    0.0000    0.0000    0.0000    0.0000    0.0000    0.0000    0.0000

8  591.0000    0.0000    0.0000    0.0000    0.0000    0.0000    0.0000    0.0000   -1.0000    0.0000    0.0000    0.0000    0.0000    0.0000    0.0000

9  350.0000    0.0000    0.0000    0.0000    0.0000    0.0000    0.0000    0.0000    0.0000   -1.0000    0.0000    0.0000    0.0000    0.0000    0.0000

10  400.0000    0.0000    0.0000    0.0000    0.0000    0.0000    0.0000    0.0000    0.0000    0.0000   -1.0000    0.0000    0.0000    0.0000    0.0000

11  400.0000    0.0000    0.0000    0.0000    0.0000    0.0000    0.0000    0.0000    0.0000    0.0000    0.0000   -1.0000    0.0000    0.0000    0.0000

12 1470.0006    0.0000    0.0000    0.0000    0.0000    0.0000    0.0000    0.0000    0.0000    0.0000    0.0000    0.0000   -1.0000    0.0000    0.0000

13 1251.0002    0.0000    0.0000    0.0000    0.0000    0.0000    0.0000    0.0000    0.0000    0.0000    0.0000    0.0000    0.0000   -1.0000    0.0000

14  684.0002    0.0000    0.0000    0.0000    0.0000    0.0000    0.0000    0.0000    0.0000    0.0000    0.0000    0.0000    0.0000    0.0000   -1.0000

LINE   0<=+RHS   -HYDRO    -COAL 1   -COAL 2   -FS#6 1   -COAL 3   -COAL 4   -COAL 5   -FS#6 2   -FS#6 3   -NUCL 1   -NUCL 2   -Area 1   -Area 2   -Area 3

10  140.0000   -0.0465    0.1283    0.1553   -0.0801   -0.0461   -0.0505   -0.0576   -0.0653   -0.0577   -0.0476   -0.0467   -0.0511    0.0545    0.0105

11  140.0000    0.0410    0.0452    0.0452   -0.9397    0.0423    0.0423    0.0420    0.0436    0.0421    0.0419    0.0417    0.0419    0.0435   -0.1686

12  140.0000   -0.0600   -0.0392   -0.0412    0.4604   -0.0630   -0.0608   -0.0566   -0.0559   -0.0567   -0.0612   -0.0612   -0.0571   -0.0500    0.2163

13  140.0000   -0.0431   -0.0745   -0.0726    0.4617   -0.0437   -0.0458   -0.0490   -0.0534   -0.0491   -0.0440   -0.0435   -0.0429   -0.0539    0.1948

23  400.0000   -0.2770    0.0948    0.0985    0.1399   -0.2761   -0.3002   -0.0884    0.1092   -0.0884   -0.2827   -0.2779   -0.1335    0.0983    0.1180

28  400.0000   -0.4327    0.0618    0.0631    0.0794   -0.0702    0.1111    0.0959    0.0889    0.0961   -0.4622   -0.3373   -0.0877    0.0679    0.0700

29  400.0000   -0.2845    0.0217    0.0247    0.0561   -0.2855   -0.3057    0.4009    0.1566    0.4011   -0.2902   -0.2860   -0.0647    0.0576    0.0411

22 1470.0000   -1.0000    0.0000    0.0000    0.0000   -1.0000   -1.0000    0.0000    0.0000    0.0000   -1.0000   -1.0000   -1.0000    0.0000    0.0000

23 1251.0000    0.0000    0.0000    0.0000    0.0000    0.0000    0.0000   -1.0000   -1.0000   -1.0000    0.0000    0.0000    0.0000   -1.0000    0.0000

24  684.0000    0.0000   -1.0000   -1.0000   -1.0000    0.0000    0.0000    0.0000    0.0000    0.0000    0.0000    0.0000    0.0000    0.0000   -1.0000

Feasible Solution

Final LP:

MAX 3392.4844   -0.9988   -1.2772   -1.2772   -1.2967   -1.0005   -1.0005   -0.9981   -1.0001   -0.9981   -0.9999   -0.9997    0.0544    0.0564   -0.2186

0<=+RHS   -HYDRO    -COAL 1   -COAL 2   -FS#6 1   -COAL 3   -COAL 4   -COAL 5   -FS#6 2   -FS#6 3   -NUCL 1   -NUCL 2   -Area 1   -Area 2   -Area 3

1         3         3         3         1         1         2         2         2         1         1         1         2         3

1  300.0000   -1.0000    0.0000    0.0000    0.0000    0.0000    0.0000    0.0000    0.0000    0.0000    0.0000    0.0000    0.0000    0.0000    0.0000

2  192.0000    0.0000   -1.0000    0.0000    0.0000    0.0000    0.0000    0.0000    0.0000    0.0000    0.0000    0.0000    0.0000    0.0000    0.0000

3  192.0000    0.0000    0.0000   -1.0000    0.0000    0.0000    0.0000    0.0000    0.0000    0.0000    0.0000    0.0000    0.0000    0.0000    0.0000

18   12.5158   -0.0012    0.2772    0.2772    1.2967    0.0005    0.0005   -0.0019    0.0001   -0.0019   -0.0001   -0.0003   -0.0544   -0.0564    0.2186

5  215.0000    0.0000    0.0000    0.0000    0.0000   -1.0000    0.0000    0.0000    0.0000    0.0000    0.0000    0.0000    0.0000    0.0000    0.0000

6  155.0000    0.0000    0.0000    0.0000    0.0000    0.0000   -1.0000    0.0000    0.0000    0.0000    0.0000    0.0000    0.0000    0.0000    0.0000

7  310.0000    0.0000    0.0000    0.0000    0.0000    0.0000    0.0000   -1.0000    0.0000    0.0000    0.0000    0.0000    0.0000    0.0000    0.0000

8  591.0000    0.0000    0.0000    0.0000    0.0000    0.0000    0.0000    0.0000   -1.0000    0.0000    0.0000    0.0000    0.0000    0.0000    0.0000

9  350.0000    0.0000    0.0000    0.0000    0.0000    0.0000    0.0000    0.0000    0.0000   -1.0000    0.0000    0.0000    0.0000    0.0000    0.0000

10  400.0000    0.0000    0.0000    0.0000    0.0000    0.0000    0.0000    0.0000    0.0000    0.0000   -1.0000    0.0000    0.0000    0.0000    0.0000

11  400.0000    0.0000    0.0000    0.0000    0.0000    0.0000    0.0000    0.0000    0.0000    0.0000    0.0000   -1.0000    0.0000    0.0000    0.0000

26 1470.0006   -1.0000    0.0000    0.0000    0.0000   -1.0000   -1.0000    0.0000    0.0000    0.0000   -1.0000   -1.0000   -1.0000    0.0000    0.0000

27 1251.0002    0.0000    0.0000    0.0000    0.0000    0.0000    0.0000   -1.0000   -1.0000   -1.0000    0.0000    0.0000    0.0000   -1.0000    0.0000

28  671.4844    0.0012   -1.2772   -1.2772   -1.2967   -0.0005   -0.0005    0.0019   -0.0001    0.0019    0.0001    0.0003    0.0544    0.0564   -1.2186

29   25.4308   -0.0047   -0.0927   -0.1197    0.1174   -0.0050   -0.0006    0.1119    0.1198    0.1120   -0.0035   -0.0044   -0.0561    0.0494    0.0303

4  287.4842    0.0012   -0.2772   -0.2772   -1.2967   -0.0005   -0.0005    0.0019   -0.0001    0.0019    0.0001    0.0003    0.0544    0.0564   -0.2186

31   99.2690    0.0032    0.1878    0.1898   -0.3166    0.0057    0.0036    0.0071    0.0059    0.0072    0.0041    0.0042   -0.0439   -0.0362    0.1629

32  118.5595    0.0005    0.1953    0.1934   -0.3461    0.0006    0.0027   -0.0043   -0.0005   -0.0043    0.0011    0.0007   -0.0284   -0.0388    0.1365

33   71.7811    0.1436    0.0171    0.0135   -0.0284    0.1426    0.1667    0.1867   -0.0109    0.1867    0.1492    0.1444   -0.1323    0.0995    0.1132

34  116.1124    0.3450    0.0055    0.0042   -0.0122   -0.0174   -0.1988   -0.0280   -0.0210   -0.0281    0.3745    0.2496   -0.0872    0.0685    0.0679

35  358.1339    0.2198    0.0152    0.0122   -0.0194    0.2208    0.2410   -0.3432   -0.0989   -0.3435    0.2255    0.2212   -0.0639    0.0585    0.0378

12    0.0000    1.0000    0.0000    0.0000    0.0000    1.0000    1.0000    0.0000    0.0000    0.0000    1.0000    1.0000    1.0000    0.0000    0.0000

13    0.0000    0.0000    0.0000    0.0000    0.0000    0.0000    0.0000    1.0000    1.0000    1.0000    0.0000    0.0000    0.0000    1.0000    0.0000

14   12.5158   -0.0012    1.2772    1.2772    1.2967    0.0005    0.0005   -0.0019    0.0001   -0.0019   -0.0001   -0.0003   -0.0544   -0.0564    1.2186

Generation loss of load   =       0.0  MW

Transmission loss of load:

due to generation only  =       0.0  MW

due to area  3 loads    =      12.5  MW

Probability of this state =    0.5466E+00

*******************************************************************************

The following is a summary of the LP output.  Only high probability states

are listed below.  The LP above is not displayed for any of the states below.

The generator states are 0=in service 1=out of service.  Generators are 1-11.

*******************************************************************************

line state:    1  outage line(s):

generator states: 1000000000 0

line overloaded :      115.7%         7-   8     RADIAL COAL8 - LOAD BUS 8 8

Feasible Solution

Generation loss of load   =     300.0  MW

Transmission loss of load:

due to generation only  =       0.0  MW

due to area  3 loads    =      28.5  MW

Probability of this state =    0.5521E-02

line state:    1  outage line(s):

generator states: 0100000000 0

line overloaded :      100.2%         6-  10     REACTOR    8 - A1 TIE 10  8

line overloaded :      113.1%         7-   8     RADIAL COAL8 - LOAD BUS 8 8

Feasible Solution

Generation loss of load   =     192.0  MW

Transmission loss of load:

due to generation only  =       0.0  MW

due to area  3 loads    =      23.8  MW

Probability of this state =    0.1115E-01

line state:    1  outage line(s):

generator states: 0010000000 0

line overloaded :      103.9%         6-  10     REACTOR    8 - A1 TIE 10  8

line overloaded :      113.1%         7-   8     RADIAL COAL8 - LOAD BUS 8 8

Feasible Solution

Generation loss of load   =     192.0  MW

Transmission loss of load:

due to generation only  =       0.0  MW

due to area  2 loads    =      28.1  MW

due to area  3 loads    =      23.8  MW

Probability of this state =    0.1115E-01

line state:    1  outage line(s):

generator states: 0001000000 0

line overloaded :      125.6%         8-   9     LOAD BUS 8 8 - A1 TIE 9   8

line overloaded :      111.9%         8-  10     LOAD BUS 8 8 - A1 TIE 10  8

Feasible Solution

Generation loss of load   =     300.0  MW

Transmission loss of load:

due to generation only  =       0.0  MW

due to area  3 loads    =     139.0  MW

Probability of this state =    0.2277E-01

line state:    1  outage line(s):

generator states: 1001000000 0

line overloaded :      112.7%         8-   9     LOAD BUS 8 8 - A1 TIE 9   8

line overloaded :      102.6%         8-  10     LOAD BUS 8 8 - A1 TIE 10  8

Feasible Solution

Generation loss of load   =     600.0  MW

Transmission loss of load:

due to generation only  =       0.0  MW

due to area  3 loads    =      69.2  MW

Probability of this state =    0.2300E-03

line state:    1  outage line(s):

generator states: 0101000000 0

line overloaded :      120.2%         8-   9     LOAD BUS 8 8 - A1 TIE 9   8

line overloaded :      101.6%         8-  10     LOAD BUS 8 8 - A1 TIE 10  8

Feasible Solution

Generation loss of load   =     492.0  MW

Transmission loss of load:

due to generation only  =       0.0  MW

due to area  3 loads    =     109.8  MW

Probability of this state =    0.4648E-03

line state:    1  outage line(s):

generator states: 0011000000 0

line overloaded :      119.9%         8-   9     LOAD BUS 8 8 - A1 TIE 9   8

line overloaded :      101.9%         8-  10     LOAD BUS 8 8 - A1 TIE 10  8

Feasible Solution

Generation loss of load   =     492.0  MW

Transmission loss of load:

due to generation only  =       0.0  MW

due to area  3 loads    =     109.2  MW

Probability of this state =    0.4648E-03

line state:    1  outage line(s):

generator states: 0000100000 0

line overloaded :      113.4%         7-   8     RADIAL COAL8 - LOAD BUS 8 8

Feasible Solution

Generation loss of load   =     215.0  MW

Transmission loss of load:

due to generation only  =       0.0  MW

due to area  3 loads    =      24.3  MW

Probability of this state =    0.2277E-01

line state:    1  outage line(s):

generator states: 0001100000 0

line overloaded :      115.9%         8-   9     LOAD BUS 8 8 - A1 TIE 9   8

line overloaded :      105.2%         8-  10     LOAD BUS 8 8 - A1 TIE 10  8

Feasible Solution

Generation loss of load   =     515.0  MW

Transmission loss of load:

due to generation only  =       0.0  MW

due to area  3 loads    =      86.5  MW

Probability of this state =    0.9489E-03

line state:    1  outage line(s):

generator states: 0000010000 0

line overloaded :      111.6%         7-   8     RADIAL COAL8 - LOAD BUS 8 8

Feasible Solution

Generation loss of load   =     155.0  MW

Transmission loss of load:

due to generation only  =       0.0  MW

due to area  3 loads    =      21.0  MW

Probability of this state =    0.2277E-01

line state:    1  outage line(s):

generator states: 0001010000 0

line overloaded :      118.8%         8-   9     LOAD BUS 8 8 - A1 TIE 9   8

line overloaded :      106.8%         8-  10     LOAD BUS 8 8 - A1 TIE 10  8

Feasible Solution

Generation loss of load   =     455.0  MW

Transmission loss of load:

due to generation only  =       0.0  MW

due to area  3 loads    =     102.4  MW

Probability of this state =    0.9489E-03

line state:    1  outage line(s):

generator states: 0000001000 0

line overloaded :      116.2%         7-   8     RADIAL COAL8 - LOAD BUS 8 8

Feasible Solution

Generation loss of load   =     310.0  MW

Transmission loss of load:

due to generation only  =       0.0  MW

due to area  3 loads    =      29.4  MW

Probability of this state =    0.2277E-01

line state:    1  outage line(s):

generator states: 0001001000 0

line overloaded :      113.0%         8-   9     LOAD BUS 8 8 - A1 TIE 9   8

line overloaded :      101.0%         8-  10     LOAD BUS 8 8 - A1 TIE 10  8

Feasible Solution

Generation loss of load   =     610.0  MW

Transmission loss of load:

due to generation only  =       0.0  MW

due to area  3 loads    =      70.9  MW

Probability of this state =    0.9489E-03

line state:    1  outage line(s):

generator states: 0000000100 0

line overloaded :      125.3%         7-   8     RADIAL COAL8 - LOAD BUS 8 8

Feasible Solution

Generation loss of load   =     591.0  MW

Transmission loss of load:

due to generation only  =       0.0  MW

due to area  3 loads    =      45.9  MW

Probability of this state =    0.2877E-01

line state:    1  outage line(s):

generator states: 0100000100 0

line overloaded :      131.5%         7-   8     RADIAL COAL8 - LOAD BUS 8 8

line overloaded :      102.7%        14-  16     SYNC COND  0 - COAL ONE   0

Feasible Solution

Generation loss of load   =     783.0  MW

Transmission loss of load:

due to generation only  =       0.0  MW

due to area  2 loads    =      64.0  MW

due to area  3 loads    =      57.1  MW

Probability of this state =    0.5871E-03

line state:    1  outage line(s):

generator states: 0010000100 0

line overloaded :      131.5%         7-   8     RADIAL COAL8 - LOAD BUS 8 8

line overloaded :      102.8%        14-  16     SYNC COND  0 - COAL ONE   0

Feasible Solution

Generation loss of load   =     783.0  MW

Transmission loss of load:

due to generation only  =       0.0  MW

due to area  2 loads    =      67.7  MW

due to area  3 loads    =      57.1  MW

Probability of this state =    0.5871E-03

line state:    1  outage line(s):

generator states: 0001000100 0

line overloaded :      102.0%         8-   9     LOAD BUS 8 8 - A1 TIE 9   8

line overloaded :      108.6%        14-  16     SYNC COND  0 - COAL ONE   0

Feasible Solution

Generation loss of load   =     891.0  MW

Transmission loss of load:

due to generation only  =       0.0  MW

due to area  2 loads    =     183.9  MW

due to area  3 loads    =       6.0  MW

Probability of this state =    0.1199E-02

line state:    1  outage line(s):

generator states: 0000100100 0

line overloaded :      131.8%         7-   8     RADIAL COAL8 - LOAD BUS 8 8

Feasible Solution

Generation loss of load   =     806.0  MW

Transmission loss of load:

due to generation only  =       0.0  MW

due to area  3 loads    =      57.7  MW

Probability of this state =    0.1199E-02

line state:    1  outage line(s):

generator states: 0000010100 0

line overloaded :      130.0%         7-   8     RADIAL COAL8 - LOAD BUS 8 8

Feasible Solution

Generation loss of load   =     746.0  MW

Transmission loss of load:

due to generation only  =       0.0  MW

due to area  3 loads    =      54.4  MW

Probability of this state =    0.1199E-02

line state:    1  outage line(s):

generator states: 0000001100 0

line overloaded :      134.6%         7-   8     RADIAL COAL8 - LOAD BUS 8 8

Feasible Solution

Generation loss of load   =     901.0  MW

Transmission loss of load:

due to generation only  =       0.0  MW

due to area  3 loads    =      62.8  MW

Probability of this state =    0.1199E-02

line state:    1  outage line(s):

generator states: 0000000010 0

line overloaded :      117.4%         7-   8     RADIAL COAL8 - LOAD BUS 8 8

Feasible Solution

Generation loss of load   =     350.0  MW

Transmission loss of load:

due to generation only  =       0.0  MW

due to area  3 loads    =      31.6  MW

Probability of this state =    0.4753E-01

line state:    1  outage line(s):

generator states: 0001000010 0

line overloaded :      111.4%         8-   9     LOAD BUS 8 8 - A1 TIE 9   8

Feasible Solution

Generation loss of load   =     650.0  MW

Transmission loss of load:

due to generation only  =       0.0  MW

due to area  3 loads    =      62.0  MW

Probability of this state =    0.1980E-02

line state:    1  outage line(s):

generator states: 0000100010 0

line overloaded :      123.9%         7-   8     RADIAL COAL8 - LOAD BUS 8 8

Feasible Solution

Generation loss of load   =     565.0  MW

Transmission loss of load:

due to generation only  =       0.0  MW

due to area  3 loads    =      43.4  MW

Probability of this state =    0.1980E-02

line state:    1  outage line(s):

generator states: 0000010010 0

line overloaded :      122.1%         7-   8     RADIAL COAL8 - LOAD BUS 8 8

Feasible Solution

Generation loss of load   =     505.0  MW

Transmission loss of load:

due to generation only  =       0.0  MW

due to area  3 loads    =      40.1  MW

Probability of this state =    0.1980E-02

line state:    1  outage line(s):

generator states: 0000001010 0

line overloaded :      126.7%         7-   8     RADIAL COAL8 - LOAD BUS 8 8

Feasible Solution

Generation loss of load   =     660.0  MW

Transmission loss of load:

due to generation only  =       0.0  MW

due to area  3 loads    =      48.5  MW

Probability of this state =    0.1980E-02

line state:    1  outage line(s):

generator states: 0000000110 0

line overloaded :      135.8%         7-   8     RADIAL COAL8 - LOAD BUS 8 8

Feasible Solution

Generation loss of load   =     941.0  MW

Transmission loss of load:

due to generation only  =       0.0  MW

due to area  3 loads    =      65.0  MW

Probability of this state =    0.2501E-02

line state:    1  outage line(s):

generator states: 0001000110 0

line overloaded :      100.9%        14-  16     SYNC COND  0 - COAL ONE   0

Feasible Solution

Generation loss of load   =    1241.0  MW

Transmission loss of load:

due to generation only  =       0.0  MW

due to area  2 loads    =      18.9  MW

Probability of this state =    0.1042E-03

line state:    1  outage line(s):

generator states: 0000000001 0

line overloaded :      118.9%         7-   8     RADIAL COAL8 - LOAD BUS 8 8

Feasible Solution

Generation loss of load   =     400.0  MW

Transmission loss of load:

due to generation only  =       0.0  MW

due to area  3 loads    =      34.2  MW

Probability of this state =    0.7453E-01

line state:    1  outage line(s):

generator states: 0100000001 0

line overloaded :      125.1%         7-   8     RADIAL COAL8 - LOAD BUS 8 8

Feasible Solution

Generation loss of load   =     592.0  MW

Transmission loss of load:

due to generation only  =       0.0  MW

due to area  3 loads    =      45.5  MW

Probability of this state =    0.1521E-02

line state:    1  outage line(s):

generator states: 0010000001 0

line overloaded :      125.1%         7-   8     RADIAL COAL8 - LOAD BUS 8 8

Feasible Solution

Generation loss of load   =     592.0  MW

Transmission loss of load:

due to generation only  =       0.0  MW

due to area  3 loads    =      45.5  MW

Probability of this state =    0.1521E-02

line state:    1  outage line(s):

generator states: 0001000001 0

line overloaded :      108.1%         8-   9     LOAD BUS 8 8 - A1 TIE 9   8

Feasible Solution

Generation loss of load   =     700.0  MW

Transmission loss of load:

due to generation only  =       0.0  MW

due to area  3 loads    =      44.0  MW

Probability of this state =    0.3106E-02

line state:    1  outage line(s):

generator states: 0000100001 0

line overloaded :      125.4%         7-   8     RADIAL COAL8 - LOAD BUS 8 8

Feasible Solution

Generation loss of load   =     615.0  MW

Transmission loss of load:

due to generation only  =       0.0  MW

due to area  3 loads    =      46.0  MW

Probability of this state =    0.3106E-02

line state:    1  outage line(s):

generator states: 0000010001 0

line overloaded :      123.5%         7-   8     RADIAL COAL8 - LOAD BUS 8 8

Feasible Solution

Generation loss of load   =     555.0  MW

Transmission loss of load:

due to generation only  =       0.0  MW

due to area  3 loads    =      42.7  MW

Probability of this state =    0.3106E-02

line state:    1  outage line(s):

generator states: 0000001001 0

line overloaded :      128.2%         7-   8     RADIAL COAL8 - LOAD BUS 8 8

Feasible Solution

Generation loss of load   =     710.0  MW

Transmission loss of load:

due to generation only  =       0.0  MW

due to area  3 loads    =      51.1  MW

Probability of this state =    0.3106E-02

line state:    1  outage line(s):

generator states: 0000000101 0

line overloaded :      137.3%         7-   8     RADIAL COAL8 - LOAD BUS 8 8

Feasible Solution

Generation loss of load   =     991.0  MW

Transmission loss of load:

due to generation only  =       0.0  MW

due to area  3 loads    =      67.6  MW

Probability of this state =    0.3923E-02

line state:    1  outage line(s):

generator states: 0000000011 0

line overloaded :      129.4%         7-   8     RADIAL COAL8 - LOAD BUS 8 8

Feasible Solution

Generation loss of load   =     750.0  MW

Transmission loss of load:

due to generation only  =       0.0  MW

due to area  3 loads    =      53.3  MW

Probability of this state =    0.6481E-02

line state:    1  outage line(s):

generator states: 0000000000 1

line overloaded :      118.8%         7-   8     RADIAL COAL8 - LOAD BUS 8 8

Feasible Solution

Generation loss of load   =     400.0  MW

Transmission loss of load:

due to generation only  =       0.0  MW

due to area  3 loads    =      34.1  MW

Probability of this state =    0.7453E-01

line state:    1  outage line(s):

generator states: 0100000000 1

line overloaded :      125.0%         7-   8     RADIAL COAL8 - LOAD BUS 8 8

Feasible Solution

Generation loss of load   =     592.0  MW

Transmission loss of load:

due to generation only  =       0.0  MW

due to area  3 loads    =      45.4  MW

Probability of this state =    0.1521E-02

line state:    1  outage line(s):

generator states: 0010000000 1

line overloaded :      125.0%         7-   8     RADIAL COAL8 - LOAD BUS 8 8

Feasible Solution

Generation loss of load   =     592.0  MW

Transmission loss of load:

due to generation only  =       0.0  MW

due to area  3 loads    =      45.4  MW

Probability of this state =    0.1521E-02

line state:    1  outage line(s):

generator states: 0001000000 1

line overloaded :      108.1%         8-   9     LOAD BUS 8 8 - A1 TIE 9   8

Feasible Solution

Generation loss of load   =     700.0  MW

Transmission loss of load:

due to generation only  =       0.0  MW

due to area  3 loads    =      43.9  MW

Probability of this state =    0.3106E-02

line state:    1  outage line(s):

generator states: 0000100000 1

line overloaded :      125.3%         7-   8     RADIAL COAL8 - LOAD BUS 8 8

Feasible Solution

Generation loss of load   =     615.0  MW

Transmission loss of load:

due to generation only  =       0.0  MW

due to area  3 loads    =      45.9  MW

Probability of this state =    0.3106E-02

line state:    1  outage line(s):

generator states: 0000010000 1

line overloaded :      123.5%         7-   8     RADIAL COAL8 - LOAD BUS 8 8

Feasible Solution

Generation loss of load   =     555.0  MW

Transmission loss of load:

due to generation only  =       0.0  MW

due to area  3 loads    =      42.6  MW

Probability of this state =    0.3106E-02

line state:    1  outage line(s):

generator states: 0001010000 1

line overloaded :      101.3%         8-   9     LOAD BUS 8 8 - A1 TIE 9   8

Feasible Solution

Generation loss of load   =     855.0  MW

Transmission loss of load:

due to generation only  =       0.0  MW

due to area  3 loads    =       7.3  MW

Probability of this state =    0.1294E-03

line state:    1  outage line(s):

generator states: 0000001000 1

line overloaded :      128.1%         7-   8     RADIAL COAL8 - LOAD BUS 8 8

Feasible Solution

Generation loss of load   =     710.0  MW

Transmission loss of load:

due to generation only  =       0.0  MW

due to area  3 loads    =      51.0  MW

Probability of this state =    0.3106E-02

line state:    1  outage line(s):

generator states: 0000000100 1

line overloaded :      137.2%         7-   8     RADIAL COAL8 - LOAD BUS 8 8

Feasible Solution

Generation loss of load   =     991.0  MW

Transmission loss of load:

due to generation only  =       0.0  MW

due to area  3 loads    =      67.6  MW

Probability of this state =    0.3923E-02

line state:    1  outage line(s):

generator states: 0000000010 1

line overloaded :      129.3%         7-   8     RADIAL COAL8 - LOAD BUS 8 8

Feasible Solution

Generation loss of load   =     750.0  MW

Transmission loss of load:

due to generation only  =       0.0  MW

due to area  3 loads    =      53.2  MW

Probability of this state =    0.6481E-02

line state:    1  outage line(s):

generator states: 0000000001 1

line overloaded :      130.8%         7-   8     RADIAL COAL8 - LOAD BUS 8 8

Feasible Solution

Generation loss of load   =     800.0  MW

Transmission loss of load:

due to generation only  =       0.0  MW

due to area  3 loads    =      55.9  MW

Probability of this state =    0.1016E-01

1

Case Title: IEEE RELIABILITY TEST SYSTEM   (GENERATORS COMBINED)

AREA  1  Area 1:

LOAD%  LOAD-MW   LOLP       TLOP       EUE-MWh    TEUE-MWh    TOTL-MWh  T/G EUE

30.0    441  0.0000000  0.0000000    0.000001    0.000000    0.000001 4.84E-11

31.0    456  0.0000001  0.0000001    0.000002    0.000001    0.000003 0.45

32.0    470  0.0000002  0.0000004    0.000004    0.000007    0.000011  1.6

33.0    485  0.0000002  0.0000004    0.000007    0.000012    0.000019  1.8

34.0    500  0.0000004  0.0000004    0.000011    0.000018    0.000029  1.7

35.0    515  0.0000006  0.0000004    0.000019    0.000024    0.000043  1.3

36.0    529  0.0000009  0.0000004    0.000030    0.000030    0.000060  1.0

37.0    544  0.0000011  0.0000004    0.000044    0.000036    0.000080 0.82

38.0    559  0.0000012  0.0000004    0.000061    0.000042    0.000103 0.69

39.0    573  0.0000015  0.0000004    0.000082    0.000048    0.000130 0.58

40.0    588  0.0000043  0.0000004    0.000114    0.000054    0.000168 0.48

41.0    603  0.0000064  0.0000004    0.000203    0.000060    0.000263 0.30

42.0    617  0.0000079  0.0000004    0.000312    0.000067    0.000378 0.21

43.0    632  0.0000121  0.0000006    0.000449    0.000076    0.000525 0.17

44.0    647  0.0000153  0.0000008    0.000651    0.000087    0.000738 0.13

45.0    662  0.0000205  0.0000008    0.000920    0.000098    0.001018 0.11

46.0    676  0.0000263  0.0000008    0.001257    0.000110    0.001367 8.72E-02

47.0    691  0.0000297  0.0000008    0.001670    0.000122    0.001792 7.30E-02

48.0    706  0.0000338  0.0000010    0.002149    0.000137    0.002286 6.37E-02

49.0    720  0.0000743  0.0000010    0.002783    0.000152    0.002935 5.45E-02

50.0    735  0.0000970  0.0000021    0.004087    0.000183    0.004269 4.47E-02

51.0    750  0.0001442  0.0000052    0.006003    0.000259    0.006262 4.31E-02

52.0    764  0.0002141  0.0000053    0.008474    0.000337    0.008810 3.98E-02

53.0    779  0.0002473  0.0000053    0.011754    0.000414    0.012168 3.53E-02

54.0    794  0.0002909  0.0000049    0.015790    0.000487    0.016276 3.08E-02

55.0    809  0.0003658  0.0000024    0.020573    0.000522    0.021095 2.54E-02

56.0    823  0.0004253  0.0000055    0.026337    0.000603    0.026939 2.29E-02

57.0    838  0.0004880  0.0000117    0.033168    0.000775    0.033943 2.34E-02

58.0    853  0.0006143  0.0000156    0.041501    0.001005    0.042506 2.42E-02

59.0    867  0.0007398  0.0000099    0.050853    0.001150    0.052003 2.26E-02

60.0    882  0.0012477  0.0000027    0.067464    0.001189    0.068653 1.76E-02

61.0    897  0.0020975  0.0000008    0.090519    0.001200    0.091719 1.33E-02

62.0    911  0.0025528  0.0000004    0.122430    0.001206    0.123636 9.85E-03

63.0    926  0.0029801  0.0000004    0.164825    0.001212    0.166038 7.36E-03

64.0    941  0.0033027  0.0000087    0.211378    0.001341    0.212719 6.34E-03

65.0    956  0.0038220  0.0000004    0.262726    0.001347    0.264073 5.13E-03

66.0    970  0.0042428  0.0000004    0.322373    0.001352    0.323725 4.20E-03

67.0    985  0.0056334  0.0000004    0.399010    0.001358    0.400368 3.40E-03

68.0   1000  0.0069255  0.0000004    0.489667    0.001364    0.491031 2.79E-03

69.0   1014  0.0075151  0.0000004    0.593606    0.001370    0.594976 2.31E-03

70.0   1029  0.0084061  0.0000004    0.714554    0.001376    0.715929 1.93E-03

71.0   1044  0.0152976  0.0000004    0.859748    0.001381    0.861130 1.61E-03

72.0   1058  0.0184925  0.0000004    1.120062    0.001387    1.121449 1.24E-03

73.0   1073  0.0219945  0.0000004    1.424062    0.001393    1.425455 9.78E-04

74.0   1088  0.0260651  0.0000004    1.770495    0.001399    1.771894 7.90E-04

75.0   1103  0.0268882  0.0000004    2.158606    0.001404    2.160010 6.51E-04

76.0   1117  0.0271659  0.0000001    2.556586    0.001406    2.557993 5.50E-04

77.0   1132  0.0398974  0.0000000    3.046995    0.001406    3.048401 4.61E-04

78.0   1147  0.0476023 -0.0000001    3.653120    0.001405    3.654525 3.85E-04

79.0   1161  0.0559507  0.0000000    4.454803    0.001405    4.456208 3.15E-04

80.0   1176  0.0692798  0.0000000    5.407555    0.001404    5.408959 2.60E-04

81.0   1191  0.0733407  0.0000000    6.441308    0.001405    6.442713 2.18E-04

82.0   1205  0.0779084  0.0000000    7.535335    0.001404    7.536738 1.86E-04

83.0   1220  0.1179339  0.0000000    8.910650    0.001404    8.912054 1.58E-04

84.0   1235  0.1252442  0.0000000   10.668993    0.001403   10.670397 1.32E-04

85.0   1250  0.1287225  0.0000000   12.535696    0.001403   12.537100 1.12E-04

86.0   1264  0.1327416  0.0000000   14.469161    0.001403   14.470565 9.70E-05

87.0   1279  0.1349223  0.0000000   16.435809    0.001403   16.437212 8.54E-05

88.0   1294  0.1351558  0.0000000   18.418924    0.001403   18.420328 7.62E-05

89.0   1308  0.2852517 -0.0000009   22.052998    0.001391   22.054388 6.31E-05

90.0   1323  0.3372858 -0.0000002   26.444802    0.001388   26.446190 5.25E-05

91.0   1338  0.3522168 -0.0000001   31.406615    0.001387   31.408003 4.42E-05

92.0   1352  0.3855689  0.0000001   36.994519    0.001388   36.995907 3.75E-05

93.0   1367  0.3855689  0.0000000   42.662346    0.001388   42.663734 3.25E-05

94.0   1382  0.4097373 -0.0000002   48.431824    0.001386   48.433208 2.86E-05

95.0   1397  0.4306520  0.0000001   54.647550    0.001387   54.648937 2.54E-05

96.0   1411  0.4534259 -0.0000002   61.163240    0.001385   61.164623 2.26E-05

97.0   1426  0.4534259  0.0000000   67.828371    0.001385   67.829758 2.04E-05

98.0   1441  0.4534259  0.0000000   74.493693    0.001385   74.495079 1.86E-05

99.0   1455  0.4534259  0.0000000   81.159075    0.001385   81.160461 1.71E-05

100.0   1470  0.7267130  0.0000000   88.159233    0.001385   88.160614 1.57E-05

1

Case Title: IEEE RELIABILITY TEST SYSTEM   (GENERATORS COMBINED)

AREA  2  Area 2:

LOAD%  LOAD-MW   LOLP       TLOP       EUE-MWh    TEUE-MWh    TOTL-MWh  T/G EUE

30.0    375  0.0000000  0.0000000    0.000001    0.000000    0.000001 ********

31.0    388  0.0000001  0.0000008    0.000002    0.000010    0.000011  6.5

32.0    400  0.0000002  0.0000008    0.000004    0.000020    0.000024  5.6

33.0    413  0.0000002  0.0000013    0.000006    0.000036    0.000042  6.1

34.0    425  0.0000004  0.0000013    0.000009    0.000053    0.000062  5.6

35.0    438  0.0000006  0.0000013    0.000016    0.000069    0.000085  4.3

36.0    450  0.0000009  0.0000013    0.000026    0.000085    0.000110  3.3

37.0    463  0.0000011  0.0000015    0.000037    0.000103    0.000141  2.8

38.0    475  0.0000012  0.0000017    0.000052    0.000124    0.000176  2.4

39.0    488  0.0000015  0.0000017    0.000070    0.000146    0.000216  2.1

40.0    500  0.0000043  0.0000017    0.000097    0.000168    0.000265  1.7

41.0    513  0.0000064  0.0000017    0.000173    0.000190    0.000362  1.1

42.0    525  0.0000079  0.0000017    0.000265    0.000212    0.000477 0.80

43.0    538  0.0000121  0.0000018    0.000382    0.000234    0.000616 0.61

44.0    550  0.0000153  0.0000018    0.000554    0.000257    0.000811 0.46

45.0    563  0.0000205  0.0000018    0.000783    0.000280    0.001063 0.36

46.0    575  0.0000263  0.0000267    0.001070    0.000614    0.001684 0.57

47.0    588  0.0000297  0.0000508    0.001421    0.001249    0.002671 0.88

48.0    600  0.0000338  0.0000508    0.001829    0.001884    0.003714  1.0

49.0    613  0.0000743  0.0000509    0.002368    0.002521    0.004889  1.1

50.0    626  0.0000970  0.0000531    0.003478    0.003185    0.006663 0.92

51.0    638  0.0001442  0.0000570    0.005108    0.003898    0.009007 0.76

52.0    651  0.0002141  0.0000571    0.007211    0.004613    0.011824 0.64

53.0    663  0.0002473  0.0000571    0.010003    0.005327    0.015329 0.53

54.0    676  0.0002909  0.0000570    0.013437    0.006040    0.019477 0.45

55.0    688  0.0003658  0.0000570    0.017508    0.006754    0.024262 0.39

56.0    701  0.0004253  0.0000570    0.022413    0.007467    0.029880 0.33

57.0    713  0.0004880  0.0000570    0.028226    0.008181    0.036407 0.29

58.0    726  0.0006143  0.0000567    0.035318    0.008889    0.044208 0.25

59.0    738  0.0007398  0.0000641    0.043277    0.009691    0.052968 0.22

60.0    751  0.0012477  0.0011011    0.057413    0.023466    0.080879 0.41

61.0    763  0.0020975  0.0012620    0.077033    0.039254    0.116287 0.51

62.0    776  0.0025528  0.0012787    0.104190    0.055251    0.159441 0.53

63.0    788  0.0029801  0.0014132    0.140270    0.072930    0.213199 0.52

64.0    801  0.0033027  0.0013703    0.179887    0.090072    0.269959 0.50

65.0    813  0.0038220  0.0012980    0.223585    0.106310    0.329896 0.48

66.0    826  0.0042428  0.0012616    0.274346    0.122093    0.396439 0.45

67.0    838  0.0056334  0.0012616    0.339566    0.137876    0.477442 0.41

68.0    851  0.0069255  0.0012616    0.416717    0.153659    0.570376 0.37

69.0    863  0.0075151  0.0012222    0.505171    0.168949    0.674120 0.33

70.0    876  0.0084061  0.0012124    0.608100    0.184116    0.792216 0.30

71.0    888  0.0152976  0.0012740    0.731663    0.200054    0.931717 0.27

72.0    901  0.0184925  0.0017403    0.953196    0.221825    1.175020 0.23

73.0    913  0.0219945  0.0026297    1.211906    0.254722    1.466628 0.21

74.0    926  0.0260651  0.0024843    1.506727    0.285800    1.792527 0.19

75.0    938  0.0268882  0.0014902    1.837017    0.304443    2.141460 0.17

76.0    951  0.0271659  0.0015135    2.175707    0.323377    2.499084 0.15

77.0    963  0.0398974  0.0015133    2.593054    0.342308    2.935362 0.13

78.0    976  0.0476023  0.0002836    3.108879    0.345856    3.454735 0.11

79.0    988  0.0559507  0.0002672    3.791127    0.349198    4.140326 9.21E-02

80.0   1001  0.0692798  0.0002545    4.601938    0.352383    4.954321 7.66E-02

81.0   1013  0.0733407  0.0002466    5.481684    0.355468    5.837152 6.48E-02

82.0   1026  0.0779084  0.0002466    6.412722    0.358553    6.771275 5.59E-02

83.0   1038  0.1179339  0.0002410    7.583143    0.361567    7.944711 4.77E-02

84.0   1051  0.1252442  0.0002371    9.079529    0.364534    9.444062 4.01E-02

85.0   1063  0.1287225  0.0002293   10.668131    0.367402   11.035533 3.44E-02

86.0   1076  0.1327416  0.0002276   12.313549    0.370249   12.683799 3.01E-02

87.0   1088  0.1349223  0.0002276   13.987206    0.373097   14.360303 2.67E-02

88.0   1101  0.1351558  0.0002276   15.674877    0.375945   16.050821 2.40E-02

89.0   1113  0.2852517  0.0001636   18.767547    0.377992   19.145538 2.01E-02

90.0   1126  0.3372858 -0.0000002   22.505061    0.377990   22.883051 1.68E-02

91.0   1138  0.3522168 -0.0000001   26.727665    0.377988   27.105654 1.41E-02

92.0   1151  0.3855689  0.0000001   31.483084    0.377990   31.861074 1.20E-02

93.0   1163  0.3855689  0.0098509   36.306519    0.501224   36.807743 1.38E-02

94.0   1176  0.4097373  0.0111544   41.216462    0.640766   41.857227 1.55E-02

95.0   1188  0.4306520  0.0040294   46.506170    0.691174   47.197346 1.49E-02

96.0   1201  0.4534259 -0.0000002   52.051154    0.691172   52.742325 1.33E-02

97.0   1213  0.4534259  0.0000000   57.723316    0.691172   58.414486 1.20E-02

98.0   1226  0.4534259  0.0000000   63.395640    0.691172   64.086815 1.09E-02

99.0   1238  0.4534259  0.0000000   69.068014    0.691172   69.759186 1.00E-02

100.0   1251  0.7267130  0.0000000   75.025290    0.691172   75.716461 9.21E-03

1

Case Title: IEEE RELIABILITY TEST SYSTEM   (GENERATORS COMBINED)

AREA  3  Area 3:

LOAD%  LOAD-MW   LOLP       TLOP       EUE-MWh    TEUE-MWh    TOTL-MWh  T/G EUE

30.0    205  0.0000000  0.0000000    0.000000    0.000000    0.000000 2.61E-10

31.0    212  0.0000001  0.0000173    0.000001    0.000119    0.000119 1.42E+02

32.0    219  0.0000002  0.0000193    0.000002    0.000251    0.000253 1.26E+02

33.0    226  0.0000002  0.0000209    0.000003    0.000393    0.000397 1.20E+02

34.0    233  0.0000004  0.0000685    0.000005    0.000862    0.000867 1.68E+02

35.0    239  0.0000006  0.0000825    0.000009    0.001426    0.001435 1.63E+02

36.0    246  0.0000009  0.0001014    0.000014    0.002119    0.002133 1.52E+02

37.0    253  0.0000011  0.0001241    0.000020    0.002968    0.002989 1.45E+02

38.0    260  0.0000012  0.0001417    0.000028    0.003937    0.003966 1.38E+02

39.0    267  0.0000015  0.0001712    0.000038    0.005108    0.005146 1.34E+02

40.0    274  0.0000043  0.0001940    0.000053    0.006435    0.006488 1.22E+02

41.0    280  0.0000064  0.0002462    0.000094    0.008119    0.008213  86.

42.0    287  0.0000079  0.0002816    0.000145    0.010045    0.010190  69.

43.0    294  0.0000121  0.0003285    0.000209    0.012292    0.012501  59.

44.0    301  0.0000153  0.0003555    0.000303    0.014723    0.015026  49.

45.0    308  0.0000205  0.0004056    0.000428    0.017498    0.017926  41.

46.0    315  0.0000263  0.0004145    0.000585    0.020333    0.020918  35.

47.0    321  0.0000297  0.0009133    0.000777    0.026580    0.027357  34.

48.0    328  0.0000338  0.0010509    0.001000    0.033768    0.034769  34.

49.0    335  0.0000743  0.0017554    0.001295    0.045775    0.047070  35.

50.0    342  0.0000970  0.0019598    0.001902    0.059181    0.061082  31.

51.0    349  0.0001442  0.0021909    0.002793    0.074167    0.076960  27.

52.0    356  0.0002141  0.0023083    0.003943    0.089956    0.093898  23.

53.0    363  0.0002473  0.0023580    0.005469    0.106084    0.111553  19.

54.0    369  0.0002909  0.0027821    0.007347    0.125113    0.132460  17.

55.0    376  0.0003658  0.0030129    0.009573    0.145722    0.155294  15.

56.0    383  0.0004253  0.0040324    0.012255    0.173303    0.185558  14.

57.0    390  0.0004880  0.0045134    0.015433    0.204174    0.219608  13.

58.0    397  0.0006143  0.0050678    0.019311    0.238838    0.258149  12.

59.0    404  0.0007398  0.0053347    0.023662    0.275328    0.298990  12.

60.0    410  0.0012477  0.0053611    0.031391    0.311998    0.343389  9.9

61.0    417  0.0020975  0.0053010    0.042119    0.348257    0.390376  8.3

62.0    424  0.0025528  0.0130768    0.056967    0.437702    0.494669  7.7

63.0    431  0.0029801  0.0139465    0.076694    0.533097    0.609791  7.0

64.0    438  0.0033027  0.0168713    0.098356    0.648497    0.746852  6.6

65.0    445  0.0038220  0.0182089    0.122248    0.773045    0.895294  6.3

66.0    451  0.0042428  0.0188341    0.150002    0.901871    1.051873  6.0

67.0    458  0.0056334  0.0180733    0.185662    1.025492    1.211154  5.5

68.0    465  0.0069255  0.0175137    0.227845    1.145286    1.373131  5.0

69.0    472  0.0075151  0.0255396    0.276209    1.319976    1.596185  4.8

70.0    479  0.0084061  0.0297404    0.332486    1.523401    1.855887  4.6

71.0    486  0.0152976  0.0441914    0.400046    1.825670    2.225716  4.6

72.0    492  0.0184925  0.0617945    0.521172    2.248345    2.769516  4.3

73.0    499  0.0219945  0.0688488    0.662625    2.719271    3.381895  4.1

74.0    506  0.0260651  0.0751685    0.823822    3.233423    4.057245  3.9

75.0    513  0.0268882  0.0742809    1.004412    3.741505    4.745917  3.7

76.0    520  0.0271659  0.0808302    1.189595    4.294383    5.483978  3.6

77.0    527  0.0398974  0.1086312    1.417785    5.037421    6.455206  3.6

78.0    534  0.0476023  0.1068057    1.699819    5.767972    7.467791  3.4

79.0    540  0.0559507  0.0976111    2.072847    6.435632    8.508479  3.1

80.0    547  0.0692798  0.0905273    2.516168    7.054839    9.571007  2.8

81.0    554  0.0733407  0.0863186    2.997180    7.645259   10.642439  2.6

82.0    561  0.0779084  0.0833184    3.506237    8.215157   11.721394  2.3

83.0    568  0.1179339  0.0638459    4.146179    8.651863   12.798042  2.1

84.0    575  0.1252442  0.1504093    4.964347    9.680662   14.645009  2.0

85.0    581  0.1287225  0.1815660    5.832935   10.922574   16.755510  1.9

86.0    588  0.1327416  0.2209336    6.732588   12.433760   19.166349  1.8

87.0    595  0.1349223  0.2326670    7.647682   14.025202   21.672884  1.8

88.0    602  0.1351558  0.2505440    8.570437   15.738924   24.309362  1.8

89.0    609  0.2852517  0.1383333   10.261394   16.685124   26.946518  1.6

90.0    616  0.3372858  0.0862154   12.304927   17.274838   29.579765  1.4

91.0    622  0.3522168  0.0710652   14.613688   17.760924   32.374611  1.2

92.0    629  0.3855689  0.0504429   17.213774   18.105953   35.319725  1.1

93.0    636  0.3855689  0.0593272   19.851048   18.511751   38.362801 0.93

94.0    643  0.4097373  0.0607003   22.535621   18.926941   41.462563 0.84

95.0    650  0.4306520  0.0308328   25.427836   19.137838   44.565674 0.75

96.0    657  0.4534259  0.0101997   28.459626   19.207604   47.667233 0.67

97.0    663  0.4534259  0.0000000   31.560952   19.207604   50.768555 0.61

98.0    670  0.4534259  0.0000000   34.662367   19.207604   53.869972 0.55

99.0    677  0.4534259  0.4535408   37.763809   22.309823   60.073631 0.59

100.0    684  0.7267130  0.5465741   41.021025   26.048391   67.069420 0.64

1

Case Title: IEEE RELIABILITY TEST SYSTEM   (GENERATORS COMBINED)

TOTAL SYSTEM:

LOAD%  LOAD-MW   LOLP       TLOP       EUE-MWh    TEUE-MWh    TOTL-MWh  T/G EUE

30.0   1022  0.0000000  0.0000000    0.000002    0.000000    0.000002 ********

31.0   1056  0.0000001  0.0000006    0.000004    0.000021    0.000025  5.0

32.0   1090  0.0000002  0.0000007    0.000010    0.000044    0.000054  4.4

33.0   1124  0.0000002  0.0000007    0.000016    0.000069    0.000085  4.2

34.0   1158  0.0000004  0.0000008    0.000025    0.000095    0.000121  3.7

35.0   1192  0.0000006  0.0000008    0.000044    0.000122    0.000165  2.8

36.0   1226  0.0000009  0.0000008    0.000070    0.000150    0.000219  2.2

37.0   1260  0.0000011  0.0000029    0.000102    0.000250    0.000352  2.5

38.0   1294  0.0000012  0.0000034    0.000142    0.000365    0.000507  2.6

39.0   1328  0.0000015  0.0000034    0.000190    0.000482    0.000672  2.5

40.0   1362  0.0000043  0.0000056    0.000263    0.000671    0.000934  2.5

41.0   1396  0.0000064  0.0000061    0.000470    0.000878    0.001348  1.9

42.0   1430  0.0000079  0.0000092    0.000723    0.001192    0.001914  1.6

43.0   1464  0.0000121  0.0000114    0.001040    0.001581    0.002621  1.5

44.0   1498  0.0000153  0.0000102    0.001507    0.001928    0.003436  1.3

45.0   1532  0.0000205  0.0000091    0.002131    0.002237    0.004369  1.0

46.0   1566  0.0000263  0.0000231    0.002912    0.003023    0.005935  1.0

47.0   1600  0.0000297  0.0000568    0.003869    0.004956    0.008825  1.3

48.0   1634  0.0000338  0.0000821    0.004979    0.007750    0.012729  1.6

49.0   1668  0.0000743  0.0000958    0.006446    0.011011    0.017457  1.7

50.0   1703  0.0000970  0.0000766    0.009466    0.013621    0.023087  1.4

51.0   1737  0.0001442  0.0000828    0.013904    0.016440    0.030345  1.2

52.0   1771  0.0002141  0.0000985    0.019628    0.019795    0.039422  1.0

53.0   1805  0.0002473  0.0001355    0.027225    0.024410    0.051635 0.90

54.0   1839  0.0002909  0.0001522    0.036574    0.029591    0.066165 0.81

55.0   1873  0.0003658  0.0001665    0.047654    0.035261    0.082915 0.74

56.0   1907  0.0004253  0.0001465    0.061004    0.040248    0.101252 0.66

57.0   1941  0.0004880  0.0003646    0.076827    0.052661    0.129489 0.69

58.0   1975  0.0006143  0.0006247    0.096131    0.073933    0.170063 0.77

59.0   2009  0.0007398  0.0013163    0.117792    0.118751    0.236543  1.0

60.0   2043  0.0012477  0.0012113    0.156268    0.159995    0.316263  1.0

61.0   2077  0.0020975  0.0010629    0.209671    0.196186    0.405857 0.94

62.0   2111  0.0025528  0.0006515    0.283587    0.218371    0.501957 0.77

63.0   2145  0.0029801  0.0005730    0.381789    0.237883    0.619672 0.62

64.0   2179  0.0033027  0.0009327    0.489621    0.269640    0.759261 0.55

65.0   2213  0.0038220  0.0020149    0.608560    0.338247    0.946807 0.56

66.0   2247  0.0042428  0.0021284    0.746720    0.410719    1.157439 0.55

67.0   2281  0.0056334  0.0014003    0.924237    0.458401    1.382638 0.50

68.0   2315  0.0069255  0.0012333    1.134229    0.500394    1.634623 0.44

69.0   2349  0.0075151  0.0027489    1.374986    0.593994    1.968979 0.43

70.0   2384  0.0084061  0.0101931    1.655139    0.941068    2.596207 0.57

71.0   2418  0.0152976  0.0114464    1.991457    1.330819    3.322276 0.67

72.0   2452  0.0184925  0.0060749    2.594429    1.537670    4.132100 0.59

73.0   2486  0.0219945  0.0050159    3.298591    1.708463    5.007054 0.52

74.0   2520  0.0260651  0.0036178    4.101043    1.831649    5.932692 0.45

75.0   2554  0.0268882  0.0036975    5.000034    1.957547    6.957581 0.39

76.0   2588  0.0271659  0.0131542    5.921886    2.405446    8.327332 0.41

77.0   2622  0.0398974  0.0157016    7.057832    2.940085    9.997916 0.42

78.0   2656  0.0476023  0.0166420    8.461816    3.506744   11.968560 0.41

79.0   2690  0.0559507  0.0134151   10.318774    3.963528   14.282303 0.38

80.0   2724  0.0692798  0.0082081   12.525658    4.243013   16.768671 0.34

81.0   2758  0.0733407  0.0072863   14.920168    4.491113   19.411282 0.30

82.0   2792  0.0779084  0.0321490   17.454288    5.585786   23.040073 0.32

83.0   2826  0.1179339  0.0294452   20.639967    6.588395   27.228363 0.32

84.0   2860  0.1252442  0.0102687   24.712862    6.938045   31.650908 0.28

85.0   2894  0.1287225  0.0068412   29.036755    7.170987   36.207741 0.25

86.0   2928  0.1327416  0.0032194   33.515289    7.280608   40.795898 0.22

87.0   2962  0.1349223  0.0013050   38.070686    7.325045   45.395733 0.19

88.0   2996  0.1351558  0.1335381   42.664227   11.872018   54.536243 0.28

89.0   3030  0.2852517  0.0714061   51.081924   14.303396   65.385323 0.28

90.0   3065  0.3372858  0.0579205   61.254772   16.275589   77.530357 0.27

91.0   3099  0.3522168  0.0460111   72.747948   17.842267   90.590218 0.25

92.0   3133  0.3855689  0.0053598   85.691353   18.024769  103.716125 0.21

93.0   3167  0.3855689  0.0024542   98.819885   18.108335  116.928223 0.18

94.0   3201  0.4097373  0.0305288  112.183876   19.147841  131.331711 0.17

95.0   3235  0.4306520  0.0119191  126.581520   19.553686  146.135208 0.15

96.0   3269  0.4534259  0.0101997  141.673981   19.900987  161.574966 0.14

97.0   3303  0.4534259  0.0000000  157.112595   19.900986  177.013580 0.13

98.0   3337  0.4534259  0.0000000  172.551651   19.900986  192.452637 0.12

99.0   3371  0.4534259  0.0000000  187.990845   19.900986  207.891830 0.11

100.0   3405  0.7267130  0.2009037  204.205490   26.741756  230.947250 0.13

:         :          :       :            :                       :

Installed         :          :       :            : Ratio of unserved energies

Generation         :          :       :            : Transmission to Generation

:          :       :            :

Probability of not          :       :   Additional unserved MWH due

serving load at             :       :   to transmission constraints

system peak hour            :       :

:       :

Probability transmission       Unserved MWH during the peak load hour

will be a bottleneck           due only to insufficient generation

full enumeration completed

Linear Program Rows       =          27         360 max

Linear Program Columns    =          15          50 max

# of infeasible states    =           1

# xmissn states examined  =           0

Prob of trans loss of load=    0.9974E+00

Prob of states examined   =    0.1000E+01

Prob of system separation =    0.0000E+00

Prob of untested sys sep  =    0.0000E+00

Prob of untested states   =    0.0000E+00

Sum of probability states =    1.000000

Full enumeration time =   0h  0m 28s

Total run time            0h  0m 30s

IEEE RTS Line Flow Distributions

80%

80%

80%

80%

80%

80%

80%

80%